## 2024 PM HTG Work Orders
Status Category | Work Order # | Source Site | Source Asset | Work Category | WO Status | Work requested | Assigned | Action Taken | Completed | Work Type
Archived | 0000015755 | Bryant Woods ES | BWES-RTU-NW | Heating/Ventilation /Air Conditioning | Archived | (RTU-NW) HVAC SUMMER PM-BWES-YEARLY | 03/19/2024 12:20:00 PM | 3/22/24- AB1 when preparing to clean coil I noticed some oil on the lower right hard side about 8 inches up from the right bottom corner. Removed the side panel to locate leak, marked where I suspect the leak to be. Checked system pressure to see if it was still holding any pressure. It was. Checked with it running and it went down bellow 20psi and cycled off on low pressure. need to return when its warmer(70+) to see what's going on. in the meantime i disconnected high pressure switch to keep from running. Resumed coil cleaning. 5/16/24-Complete | 05/16/2024 02:30:00 PM | Preventive Maintenance
Archived | 0000015756 | Bryant Woods ES | BWES-RTU-SE | Heating/Ventilation /Air Conditioning | Archived | (RTU-SE) HVAC PM-BWES-YEARLY | 03/19/2024 12:20:00 PM | 3/20/24-AB1 Cleaned coil 4/1024- AB1 Completed PM | 04/10/2024 02:18:00 PM | Preventive Maintenance
Archived | 0000015754 | Bryant Woods ES | BWES-RTU-MC | Heating/Ventilation /Air Conditioning | Archived | (RTU-MC) HVAC SUMMER PM-BWES-YEARLY | 03/19/2024 12:20:00 PM | 3/19/24- AB1 Prepared for coil cleaning by bringing 200ft hose, pump spayer and solution up to roof. 3/21/24- AB1 Cleaned Condenser Coil 4/10/24- Finished PM | 04/10/2024 02:13:00 PM | Preventive Maintenance
Archived | 0000015752 | Bryant Woods ES | BWES-RTU-O | Heating/Ventilation /Air Conditioning | Archived | (RTU-O) HVAC SUMMER PM-BWES-YEARLY | 03/19/2024 12:20:00 PM | 3/20/24- Cleaned condenser coil. 4/10/24-Finished PM | 04/10/2024 02:12:00 PM | Preventive Maintenance
Archived | 0000015751 | Bryant Woods ES | BWES-RTU-MP | Heating/Ventilation /Air Conditioning | Archived | (RTU-MP) HVAC SUMMER PM-BWES-YEARLY | 03/19/2024 12:20:00 PM | 3/20/24- Cleaned condenser coil. 4/10/24- Finished PM | 04/10/2024 02:11:00 PM | Preventive Maintenance
Archived | 0000015750 | Bryant Woods ES | BWES-RTU-KA | Heating/Ventilation /Air Conditioning | Archived | (RTU-KA) HVAC SUMMER PM-BWES-YEARLY | 03/19/2024 12:20:00 PM | 4/9- Cleaned coil 4/10-Finished PM | 04/10/2024 02:09:00 PM | Preventive Maintenance
Archived | 0000015753 | Bryant Woods ES | BWES-RTU-NE | Heating/Ventilation /Air Conditioning | Archived | (RTU-NE) HVAC SUMMER PM-BWES-YEARLY | 03/19/2024 12:20:00 PM | 3/21/24- AB1 Cleaned Condenser Coil 4/10/24- Finished PM | 04/10/2024 02:08:00 PM | Preventive Maintenance
Assigned | 0000015758 | Bryant Woods ES | BWES-RTU-01 | Heating/Ventilation /Air Conditioning | New PM Work Order | (RTU GYM) HVAC SUMMER PM-BWES-YEARLY | 03/19/2024 12:20:00 PM |  |  | Preventive Maintenance
Assigned | 0000015757 | Bryant Woods ES | BWES-RTU-SW | Heating/Ventilation /Air Conditioning | In Progress | (RTU-SW) HVAC SUMMER PM-BWES-YEARLY | 03/19/2024 12:20:00 PM |  |  | Preventive Maintenance
Archived | 0000016875 | Bryant Woods ES |  | Filters | Archived | FILTER 1'-BWES-QUARTERLY | 04/01/2024 01:18:00 AM | BH-1 Wednesday 4-3-24 Pulled 1" filters for school. Replaced indoor filter, replaced filters for portables and washed filters for portables using spray 9, coil brush & non-rinse evap foam spray. Completed 1" filter replacement and stored old filters in van for later disposal. | 04/08/2024 07:50:00 AM | Preventive Maintenance
Archived | 0000022104 | Bryant Woods ES | BWES-PORTABLE-113 | Heating/Ventilation /Air Conditioning | Archived | OA DAMPER PORTABLE CHECK BWES VERIFY THAT THE OADs MOVE FREELY AND ALSO ADJUST THEM TO A 25% POSITION WHEN THEY ARE OPEN (0% POSITION WHEN THEY ARE CLOSED) | 05/10/2024 06:52:00 AM | 5/15/24- OA Control Not Available(No actuator) removed pins so barometric damper has full range of motion | 05/17/2024 02:38:00 PM | Preventive Maintenance
Archived | 0000022105 | Bryant Woods ES | BWES-PORTABLE-118 | Heating/Ventilation /Air Conditioning | Archived | OA DAMPER PORTABLE CHECK BWES VERIFY THAT THE OADs MOVE FREELY AND ALSO ADJUST THEM TO A 25% POSITION WHEN THEY ARE OPEN (0% POSITION WHEN THEY ARE CLOSED) | 05/10/2024 06:52:00 AM | 5/15/24- OA Control Not Available(No actuator) removed pins so barometric damper has full range of motion | 05/15/2024 02:21:00 PM | Preventive Maintenance
Archived | 0000022106 | Bryant Woods ES | BWES-PORTABLE-126 | Heating/Ventilation /Air Conditioning | Archived | OA DAMPER PORTABLE CHECK BWES VERIFY THAT THE OADs MOVE FREELY AND ALSO ADJUST THEM TO A 25% POSITION WHEN THEY ARE OPEN (0% POSITION WHEN THEY ARE CLOSED) | 05/10/2024 06:52:00 AM | 5/15/24- OA Control Not Available(No actuator) removed pins so barometric damper has full range of motion | 05/15/2024 02:16:00 PM | Preventive Maintenance
Archived | 0000022107 | Bryant Woods ES | BWES-PORTABLE-204 | Heating/Ventilation /Air Conditioning | Archived | OA DAMPER PORTABLE CHECK BWES VERIFY THAT THE OADs MOVE FREELY AND ALSO ADJUST THEM TO A 25% POSITION WHEN THEY ARE OPEN (0% POSITION WHEN THEY ARE CLOSED) | 05/10/2024 06:52:00 AM | Unit designed for fixed outdoor air(No actuator/control). Manual set damper for 10% OA | 05/15/2024 02:11:00 PM | Preventive Maintenance
Archived | 0000022108 | Bryant Woods ES | BWES-Portable-234 | Heating/Ventilation /Air Conditioning | Archived | OA DAMPER PORTABLE CHECK BWES VERIFY THAT THE OADs MOVE FREELY AND ALSO ADJUST THEM TO A 25% POSITION WHEN THEY ARE OPEN (0% POSITION WHEN THEY ARE CLOSED) | 05/10/2024 06:52:00 AM | 5/15/24- Found miswiring issue on low voltage terminal block. After correcting miswiring issue, the actuator started operating as it should. Adjusted OA percentage to 20%. Cycled power to make sure it closed(0%) on power off and opened(20%) on power on. | 05/15/2024 02:05:00 PM | Preventive Maintenance
Archived | 0000022109 | Bryant Woods ES | BWES-PORTABLE-257 | Heating/Ventilation /Air Conditioning | Archived | OA DAMPER PORTABLE CHECK BWES VERIFY THAT THE OADs MOVE FREELY AND ALSO ADJUST THEM TO A 25% POSITION WHEN THEY ARE OPEN (0% POSITION WHEN THEY ARE CLOSED) | 05/10/2024 06:52:00 AM | 5/15/24- Found miswiring issue on low voltage terminal block. After correcting miswiring issue, the actuator started operating as it should. Adjusted OA percentage to 20%. Cycled power to make sure it closed(0%) on power off and opened(20%) on power on. | 05/15/2024 01:48:00 PM | Preventive Maintenance
Archived | 0000022110 | Bryant Woods ES | BWES-PORTABLE-258 | Heating/Ventilation /Air Conditioning | Archived | OA DAMPER PORTABLE CHECK BWES VERIFY THAT THE OADs MOVE FREELY AND ALSO ADJUST THEM TO A 25% POSITION WHEN THEY ARE OPEN (0% POSITION WHEN THEY ARE CLOSED) | 05/10/2024 06:52:00 AM | 5/13/24- Discovered Damper actuator not operational. Due to loss of voltage. Found that indoor blower relay coil has no continuity and needs to be replaced. Will get replacement part asap. 5/15/24- Replaced blower relay, and found miswiring issue on low voltage terminal block. After correcting miswiring issue, the actuator started operating as it should. Adjusted OA percentage to 20%. Cycled power to make sure it closed on power off and opened on power on. | 05/15/2024 01:35:00 PM | Preventive Maintenance
Archived | 0000028167 | Bryant Woods ES | BWES-PORTABLE-258 | Heating/Ventilation /Air Conditioning | Archived | PORTABLE TEMP-BWES-SUMMER | 07/01/2024 01:21:00 AM | Set to 82 | 07/10/2024 01:26:00 PM | Preventive Maintenance
Archived | 0000028166 | Bryant Woods ES | BWES-PORTABLE-257 | Heating/Ventilation /Air Conditioning | Archived | PORTABLE TEMP-BWES-SUMMER | 07/01/2024 01:21:00 AM | 7/09/24- Set to 82, but noticed that portable was several degrees above setpoint. Will need to figure out why unit is not cooling enough. | 07/10/2024 01:24:00 PM | Preventive Maintenance
Archived | 0000028165 | Bryant Woods ES | BWES-Portable-234 | Heating/Ventilation /Air Conditioning | Archived | PORTABLE TEMP-BWES-SUMMER | 07/01/2024 01:21:00 AM | Set to 82 | 07/10/2024 01:20:00 PM | Preventive Maintenance
Archived | 0000028164 | Bryant Woods ES | BWES-PORTABLE-204 | Heating/Ventilation /Air Conditioning | Archived | PORTABLE TEMP-BWES-SUMMER | 07/01/2024 01:21:00 AM | Changed to 82 | 07/10/2024 01:17:00 PM | Preventive Maintenance
Archived | 0000028163 | Bryant Woods ES | BWES-PORTABLE-118 | Heating/Ventilation /Air Conditioning | Archived | PORTABLE TEMP-BWES-SUMMER | 07/01/2024 01:21:00 AM | Changed to 82 | 07/10/2024 01:15:00 PM | Preventive Maintenance
Archived | 0000028162 | Bryant Woods ES | BWES-PORTABLE-113 | Heating/Ventilation /Air Conditioning | Archived | PORTABLE TEMP-BWES-SUMMER | 07/01/2024 01:21:00 AM | Changed to 82 | 07/10/2024 01:12:00 PM | Preventive Maintenance
Archived | 0000031630 | Bryant Woods ES | BWES-Boiler-1 | Boiler | Archived | Boiler PM-Bryant Woods ES-Yearly | 08/01/2024 01:18:00 AM | 09/30/2024.(RM2). Complete applicable items on task list. | 10/01/2024 07:20:00 AM | Preventive Maintenance
Archived | 0000031767 | Bryant Woods ES | BWES-PORTABLE-204 | Heating/Ventilation /Air Conditioning | Archived | PORTABLE TEMP-BWES-WINTER | 08/01/2024 01:21:00 AM | 8/01/24- Changed temp setpoint and batteries on thermostat. Tested operation. | 08/02/2024 09:10:00 AM | Preventive Maintenance
Archived | 0000031766 | Bryant Woods ES | BWES-PORTABLE-118 | Heating/Ventilation /Air Conditioning | Archived | PORTABLE TEMP-BWES-WINTER | 08/01/2024 01:21:00 AM | 8/01/24- Changed temp setpoint and batteries on thermostat. Tested operation. | 08/02/2024 09:07:00 AM | Preventive Maintenance
Archived | 0000031765 | Bryant Woods ES | BWES-PORTABLE-113 | Heating/Ventilation /Air Conditioning | Archived | PORTABLE TEMP-BWES-WINTER | 08/01/2024 01:21:00 AM | 8/01/24- Changed temp setpoint and batteries on thermostat. Tested operation. | 08/02/2024 09:05:00 AM | Preventive Maintenance
Archived | 0000031768 | Bryant Woods ES | BWES-Portable-234 | Heating/Ventilation /Air Conditioning | Archived | PORTABLE TEMP-BWES-WINTER | 08/01/2024 01:21:00 AM | 8/01/24- Changed temp setpoint and batteries on thermostat. Tested operation. | 08/02/2024 08:58:00 AM | Preventive Maintenance
Archived | 0000031769 | Bryant Woods ES | BWES-PORTABLE-257 | Heating/Ventilation /Air Conditioning | Archived | PORTABLE TEMP-BWES-WINTER | 08/01/2024 01:21:00 AM | 8/1/24- Changed temp setpoint and batteries on thermostat and tested operation. | 08/02/2024 08:54:00 AM | Preventive Maintenance
Archived | 0000031770 | Bryant Woods ES | BWES-PORTABLE-258 | Heating/Ventilation /Air Conditioning | Archived | PORTABLE TEMP-BWES-WINTER | 08/01/2024 01:21:00 AM | 8/01/24- Set to 76 but after realizing that it was not cooling. I looked in to it and found that Bard unit was low on refrigerant. Recovered .89 lb of refrigerant. Pressure tested with 450PSI Nitrogen for an hour. Because it passed the pressure test, I evacuated to 500Microns. Standing vacuum test-passed. Charged with nameplate charge of 4.5lb 410A | 08/02/2024 08:51:00 AM | Preventive Maintenance
Assigned | 0000039391 | Bryant Woods ES |  | Filters | New PM Work Order | FILTER 1'-BWES-QUARTERLY | 10/01/2024 01:18:00 AM |  |  | Preventive Maintenance

## 2024 NON PM HTG Work Orders
Assigned To Department | Status Category | Work Order # | Source Site | Source Asset | Work Category | Work requested | Assigned | Action Taken | Completed | Work Type
HVAC | Archived | 0000037461 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | A tube ripped need replace in the kiln closet. | 09/12/2024 08:59:00 AM | Picked up new kiln vent 5" flexible rigid round duct from from RE Michel and installed. | 09/20/2024 02:41:00 PM | General Maintenance
HVAC | Archived | 0000038361 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Ceiling leak tile filled with water | 09/20/2024 11:34:00 AM | Leak directly under condensate pump. Kink on outlet of pump. Cleared kink and tested. All good. | 09/20/2024 02:31:00 PM | General Maintenance
HVAC | Archived | 0000037946 | Bryant Woods ES |  | Boiler | HEATING EQUIPMENT GENERAL OPERATION CHECK. | 09/17/2024 10:13:00 AM | 09/17/2024. (RM2). Visit site. Checked equipment for water leaks. Checked building heating pump operation. Checked boiler circulator pump operation. Checked combustion damper operation. Checked the current operating pressure. Checked the burner control sequence of operation. Checked the gas valve operation. Monitored operation. Filled in Asset Essentials ticket. | 09/18/2024 06:48:00 AM | Boiler
HVAC | Archived | 0000037323 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | A/c not working temp 78 room feels wram was told need coolant | 09/11/2024 12:11:00 PM | 9/12/24- Charge unit with 3 lbs 410A Tested operation. | 09/17/2024 11:45:00 AM | General Maintenance
HVAC | Archived | 0000037305 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Front office - cold Art room- warm | 09/11/2024 08:37:00 AM | 9/3/24- Checked temp in art room and checked calibration of stat. Checked volume damper at minimum heating position, and maximum cooling position. Found the not enough volume of air for cooling. Adjusted cooling position setpoint. Checked for air flow. Checked temp in office and checked thermostat calibration. Thermostat a couple degrees off. Recalibrated stat. And checked for warmer air from supply registers. 9/12/24- Checked both areas. Both areas seem to be okay now. | 09/11/2024 08:47:00 AM | General Maintenance
HVAC | Archived | 0000036914 | Bryant Woods ES | BWES-Boiler-1 | Boiler | BOILER PM AND SAFETY DEVICE EXERCISE. | 09/06/2024 12:34:00 PM | 09/06/2024.(RM2).Check boiler for water leaks, check current operating pressure @ 30 PSI, check building pump operation, check circulator pump operation, check the burner control sequence of operation, check the combustion damper operation, flush the LWCO, flush the SRV, exercise the safety devices, check the email alert response, check the log sheet, monitor operation. Filled in Asset Essentials ticket. | 09/09/2024 07:19:00 AM | Boiler
HVAC | Archived | 0000035669 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Teacher let me know her classroom was getting warm | 08/29/2024 12:53:00 PM | 8/27/24- Thermostat display reading a p8 error code. Troubleshot unit and found that low pressure switch was open. Low refrigerant. Recover and recharge 6lb 10oz R410A and test operation. | 08/29/2024 01:06:00 PM | General Maintenance
HVAC | Archived | 0000033249 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Dennis determined that the exhaust fan is drawing too many CFMs and causing the building to be in a negative pressure, higher humidity levels, and not as efficient cooling | 08/13/2024 11:00:00 AM | 8/05/24- Worked with Dennis, took measurements and determined that increasing pulley size is not a feasible option due to not enough clearance between Motor and Drive Shafts. Considering motor change to a lower RPM motor from 1725 rpm to approximately 1140 rpm motor. Called Grainger to see if they had any solutions and they didn't have any motors in the frame and rpm specs we need. Further investigation needed. 8/07/24- Called House of Balance to see if they had a motor solution available. Emailed specs and awaiting response. 8/27/24- Checked air flow and operation due to concerns about elevated Gym temperature | 08/29/2024 12:52:00 PM | General Maintenance
HVAC | Archived | 0000034493 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Replace Gym exhaust motor to move less air and to resolve building negative pressure issue. | 08/21/2024 10:39:00 AM | 8/21/24 Loaded motor at shop from House of Balance and installed, removed motor off of roof and placed in boiler room checked operation and building pressure 8/27/24- Complaints of Gym "Not Cooling." Informed that Gym unit was not designed to cool only to heat and supply fresh outdoor air. And that the Exhaust Fan is helping but can only do so much on these hotter days. Visually inspected exhaust fan and Gym unit to identify any problems. Repaired outdoor air linkage that was lose. | 08/28/2024 12:25:00 PM | General Maintenance
HVAC | Archived | 0000034834 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Heat is blaring in this room all week around 11:00 a.m. | 08/26/2024 08:35:00 AM | 8/27/24- AB1 Thermostat a few degrees out of calibration. Recalibrated and monitored operation. | 08/28/2024 12:15:00 PM | General Maintenance
HVAC | Archived | 0000033256 | Bryant Woods ES | BWES-Boiler-1 | Boiler | BOILER PM AND SAFETY DEVICE EXERCISE. | 08/13/2024 11:55:00 AM | 08/13/2024. (RM-2). Check boiler for water leaks, check current operating pressure @ 30 PSI, check building pump operation, check circulator pump operation, check the burner control sequence of operation, check the combustion damper operation, flush the LWCO, flush the SRV, exercise the safety devices, check the email alert response, check the log sheet, monitor operation. Filled in Asset Essentials ticket. | 08/14/2024 08:17:00 AM | Boiler
HVAC | Archived | 0000030053 | Bryant Woods ES | BWES-RTU-NE | Heating/Ventilation /Air Conditioning | Not cooling | 07/16/2024 07:49:00 AM | 7/15/24-AB1- Fan Cmd On Status OFF. Fuse on one phase on the disconnect blown. Need to investigate. 7/16/24- AB1- Checked wiring looking for lose connections and checking for grounds. Replaced fuse, and left the other in electrical panel as a spare. 7/17/24- RTU NE Unit tripped again due to main fuse. Continued to look for lose connections and check caps/motor windings with meter. Found one of the condenser fan capacitor that was bad. Replaced with one in stock in mechanical room. | 08/01/2024 08:03:00 AM | General Maintenance
HVAC | Archived | 0000025867 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Humidity Issue in Building. 115 and 118 overcooling. | 06/06/2024 02:42:00 PM | 6/6/24- checked VAV in 118, found that it was overcooling due to reheat water flow. Flushed coil, and got some flow. Not able to remove strainer due to stripped threads. Air volume also needed to be adjusted for heating, it was set to high. Adjusted volume control for lower heating flow set point. checked VAV in 116 found that it was overcooling due to reheat water flow. Flushed coil, and got some flow. Not able to remove strainer due to stripped threads. Air volume also needed to be adjusted for heating, it was set to high. Adjusted volume control for lower heating. Also discovered compromised insulation on the mini split in the workroom, because of the elevated humidity it was sweating and dripping on the floor. Will need to replace the insulation. 7/18/24- Art room 127 overcooling due to thermostat calibration, and likely tampering by teacher or student(security cover loose) condensate leakage from rtu-ka duct. Building pressure negative and drawing in humid air in ceiling. Dennis adjusted RTU minimum position. 131- Duct sweating for same reason but discovered that reheat valve was not opening due to thermostat calibration, also noticed that air flow not balance. Adjusted volume control to correct Hi and Lo pressures. 7/19/24- Checked thermostat setpoints and adjusted to make sure all set to the same temperature. Took room temps, and humidity levels in SE classrooms and office area. 7/22/24- Checked thermostat setpoints and adjusted to make sure all set to the same temperature. Took room temps, and humidity levels. in NE area classrooms 7/24/24- Checked thermostat setpoints and adjusted to make sure all set to the same temperature. Took room temps, and humidity levels in NW classrooms and office area. 7/25/24- Checked thermostat setpoints and adjusted to make sure all set to the same temperature. Took room temps, and humidity levels in SE are classrooms 7/26/24- Checked thermostat setpoints and adjusted to make sure all set to the same temperature. Took room temps, and humidity levels in SW are classrooms 7/29/24- Checked thermostat setpoint and adjusted to make sure all set to the same temperature. Took room temps, and humidity levels in Office, and KA areas. 7/30/24- Calibrated VAV controllers that had issues (O-3 155/150, KA-2) 7/31/24- Calibrated VAV controllers that had issues (NE-8 102/102, NE-1 112/105, NW-5 128/116, NW-3 126/open area) and emailed Larson with findings. | 08/01/2024 07:45:00 AM | General Maintenance
HVAC | Archived | 0000029556 | Bryant Woods ES | BWES-Boiler-1 | Boiler | BOILER PM AND SAFETY DEVICE EXERCISE. | 07/10/2024 10:58:00 AM | 07/10/2024. (RM-2). Check boiler for leaks, check building pump operation, check circulator pump operation, check combustion damper operation, check current operating pressure @ 15 PSI, check sequence of operation, exercise safety device, check text alarm response, (NONE), check gas valve and linkage operation, flush LWCO, flush SRV, check boiler log sheet, monitor operation. Filled in Asset Essentials ticket. | 07/11/2024 07:29:00 AM | Boiler
HVAC | Archived | 0000026291 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Due to overcooling issue its become apparent that the building had flow issues that need to be addressed. Pull strainers and clean. Flush Coil(Both directions) Check 3 way valve for proper flow direction, and operation. | 06/12/2024 10:35:00 AM | 6/11/24- Looked at BAS graphic an building map to check for sensor locations for all zones, associated rooms, and RTU. Wrote down all room numbers on note paper for documentation of work. Picked up water leak diversion kit and short hose from warehouse to expedite process. Checked temperatures to locate areas to address first. 6/24/24- Flushed Coil, Pulled/Clean Strainer, and Checked 3 Way Valve Flow direction on VAVs RTU SW: 128, 129, 130, 131, 132, SW Common Area RTU SE: 133,134,136, 137, 138, 139, 140, and 175. RTU NW: 116, 115, 114, 113,112, and185 6/25/24- RTU KA: 117, 119, 120, 121, 122,123, and 127 RTU NE: 101, 102, 103, 104, 105,106, 107, 108,109,110,111, 180 RTU O: 154,155, and 153 6/26/24-Flushed Coil, Pulled/Clean Strainer, and Checked 3 Way Valve Flow direction on VAVs: RTU O: 152, 151, 150, 149, and 148 | 06/12/2024 11:25:00 AM | General Maintenance
HVAC | Archived | 0000025922 | Bryant Woods ES | BWES-Boiler-1 | Boiler | BOILER PM AND SAFETY DEVIE EXERCISE. | 06/07/2024 09:05:00 AM | 06/07/2024.(RM-2). Check boiler for water leaks, check current operating pressure @ 30 PSI, check building pump operation, check circulator pump operation, check the burner control sequence of operation, check the combustion damper operation, flush the LWCO, flush the SRV, exercise the safety devices, check the email alert response, check the log sheet, monitor operation. | 06/10/2024 09:12:00 AM | Boiler
HVAC | Archived | 0000023378 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | The Gym has been reading 89 to 90 degrees all day walls sweating., Is there any fans that can be put in the gym for air ciculation? | 05/23/2024 07:28:00 AM | 6/05/24- We have made some changes to the units Occupied operation to provide more air exchange and movement throughout the day that will hopefully make space slightly more comfortable. Repaired EF1 an that will hopefully help some. | 06/06/2024 08:37:00 AM | General Maintenance
HVAC | Archived | 0000023580 | Bryant Woods ES | BWES-Boiler-1 | Boiler | BOILER PM AND SAFETY DEVICE EXERCISE. | 05/24/2024 09:18:00 AM | 05/24/2024.(RM-2). Check boiler for water leaks, check current operating pressure @ 30 PSI, check building pump operation, check circulator pump operation, check the burner control sequence of operation, check the combustion damper operation, flush the LWCO, flush the SRV, exercise the safety devices, check the email alert response, check the log sheet, monitor operation. Filled in Asset Essentials ticket. | 05/28/2024 06:59:00 AM | Boiler
Facilities Admins | Archived | 0000021174 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Thermostat need to be changed out with Combo sensors. Temperature, Humidity, CO2 | 05/02/2024 06:26:00 AM | On Comments section. 5/7/24: Picked up the county vehicle from the shop, went to Bryant woods, met Dennis there, started pulling new thermostat cable for RT-SE, had to fish wires thru the wall and the spaces, terminated on both side, thermosts online Started on RT-SW, hard pull, fished thru walls and spaces, terminated on both sides, thermostat is online, Dennis calibrated both sensors, Pulled programs of both units, added the new combo sensors to the program Downloaded both, mapped in the points on the server, pulled up the graphics, added RH and CO-2 to each units graphics, downloaded the server, verified all readings after download is complete. | 05/09/2024 01:32:00 PM | General Maintenance
HVAC | Archived | 0000021365 | Bryant Woods ES | BWES-Boiler-1 | Boiler | BOILER PM AND SAFETY DEVICE EXERCISE. | 05/03/2024 11:39:00 AM | 05/03/2024.(RM-2). Check boiler for water leaks, check current operating pressure @ 30 PSI, check building pump operation, check circulator pump operation, check the burner control sequence of operation, check the combustion damper operation, flush the LWCO, flush the SRV, exercise the safety devices, check the email alert response, check the log sheet, monitor operation. | 05/06/2024 07:48:00 AM | Boiler
HVAC | Archived | 0000020989 | Bryant Woods ES | BWES-RTU-NW | Heating/Ventilation /Air Conditioning | Notified of a refrigerant leak on the NW unit | 05/01/2024 07:06:00 AM | 4/30- I was told that the tech in charge of the school had found a refrigerant leak that needed to be repaired on the unit. Met up with him and we were able to pinpoint it to a U-bend on the condensing coil. Pulled the refrigerant from circuit 1 thinking that this was the circuit with the leak. Discovered, after recovering the refrigerant, that the leak was on circuit 2. Recovered the refrigerant from circuit 2 as well. Patched the leak. Pressure tested both circuits and checked again for leaks. No other leaks discovered. Triple evacuated circuit 1. Picked up refrigerant from Aireco. Charged circuit 1 up and got it to provide cooling to the space below. Started the triple evac process on circuit 2 but ran out of time. I will return tomorrow to continue working on it. 5/1- Completed the triple evac on circuit 2 and charged it. No further leaks or issues found. | 05/02/2024 07:18:00 AM | General Maintenance
HVAC | Archived | 0000019535 | Bryant Woods ES | BWES-Boiler-1 | Heating/Ventilation /Air Conditioning | BOILER PM AND SAFETY DEVICE EXERCISE. | 04/24/2024 08:22:00 AM | 04/24/2024.(RM-2). Check boiler for water leaks, check current operating pressure @ 30 PSI, check building pump operation, check circulator pump operation, check the burner control sequence of operation, check the combustion damper operation, flush the LWCO, flush the SRV, exercise the safety devices, check the email alert response, check the log sheet, monitor operation, filled in Asset Essentials ticket. | 04/26/2024 08:57:00 AM | Boiler
HVAC | Archived | 0000018565 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | The temperature in room 115 is about 80 degrees | 04/16/2024 11:19:00 AM | 4/16/24- AB1 found airline on heating valve actuator off. Clipped back tubing and reinstalled. Tested operation. Seems to be fine now. | 04/16/2024 11:24:00 AM
HVAC | Archived | 0000018650 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | room is overheating | 04/16/2024 08:10:00 AM | Checked VAV and found hot water reheat valve was open allowing the room to overheat. HVAC mechanic who is working in this school is aware of the room and has been getting the parts needed to fix this issue. Hot water valve has been turned off so that room can maintain temperature. | 04/16/2024 08:18:00 AM | General Maintenance
HVAC | Archived | 0000017818 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | The reading in gym is 87 -89 degress on walls , Vents reading 100.1 degress did (2) Two readings | 04/09/2024 11:56:00 AM | 4/9/24- Checked temperature. Almost 80 degrees in space. Checked BAS, and used override commands to trouble shoot. Heating output on BAS 0% so doesn't seemed to be the programming. Checked control cabinet and found Heating EPC at 10PSI(not heating) however on the Branch of the EPC there is a Siemens PE switch for heating that was set to 10PSI(heating) Dialed PE switch down just bellow 6PSI to get Heating operation to stop. Let Dennis know of the problem, and my temporary fix. BAS team will still need to address the issue. | 04/10/2024 02:10:00 PM
HVAC | Archived | 0000015266 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Check temperatures, Flush coils throughout building as needed, and clean filters in mini splits. | 03/14/2024 02:44:00 PM | 3/13/24- AB1 Flushed coil in Rm 130 and 129, Responding to a teacher letting me know that her room was especially cold on 3/11/24 3/19/23- AB1 Flushed coil in 131. Checked in with teachers and took temperatures in rooms 132-140, and 175. No noted issues, aside from having to calibrate stat in 132. Checked temps in Media Center, 122, and 123- temperatures okay. Cleaned mini split filter in Computer Lab room 123. Checked temperatures in 112-121, and 185- temps normal. Checked temperatures in 101-111, and Admin area- temps normal. Cleaned mini split filters in Workroom, and MDF Room. Cafeteria, Gym, and Gym Office-temps normal. | 03/19/2024 12:14:00 PM | Preventive Maintenance
HVAC | Archived | 0000014766 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Please adjust temperature. Classroom@ 60 degrees | 03/18/2024 06:44:00 AM | 3/19/24- See ticket 15266 to see repair and time. Checked temperature in space today, and its operating as it should now. | 03/19/2024 07:42:00 AM | General Maintenance
HVAC | Archived | 0000013894 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Assist EASI, with pulley removal. | 03/01/2024 12:10:00 PM | 3/01/24- AB1 Assisted EASI with pulley removal, motor replacement, and belt alignment on RTKA-ART Unit 3/15/24- AB1 Walk through building checking temperatures and noting any larger swings. all is well at this time. | 03/15/2024 12:07:00 PM | General Maintenance
HVAC | Archived | 0000014462 | Bryant Woods ES |  | Indoor Air Quality | Always keep the work order as an IEQ craft. Pictures are attached to this work order and are very important part of it and should be reviewed thoroughly to understand the findings properly: Rooftop unit (RTU-SW)- Unit was initially running but later in the walk through it suddenly shut down. Don't know if some thing happened or it was turned off remotely. This needs to be looked at by the HVAC shop at Building Maintenance. Portable # 118 and 234- Fans were in "ON" position instead of "AUTO". Changed them to "AUTO" position while on site. Rooftop unit (RTU-O)-broken condensate drain line. Tool box, misc. tools, black trash bag sitting next RTU-SW on the roof. | 03/06/2024 01:36:00 PM | 3/13/24- BAS group are working on control over-hall upgrade, adding vfds, and new motors to all RTUS. They are still working today but expect to be finished by 3/14/24. The condensate drain has been fixed. Tools, bags, and box will be removed after project is finished. Fan operation in 118 and 234 were already set to auto. | 03/13/2024 01:47:00 PM | General Maintenance
HVAC | Archived | 0000014243 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | BOILER PM AND SAFETY DEVICE EXERCISE. | 03/05/2024 09:59:00 AM | 3/5/2024.(RM-2).. (RM-2). Check boiler for water leaks, check current operating pressure @ 30 PSI, check building pump operation, check circulator pump operation, check the burner control sequence of operation, check the combustion damper operation, flush the LWCO, flush the SRV, exercise the safety devices, check the email alert response, check the log sheet, monitor operation. | 03/06/2024 07:15:00 AM | Boiler
HVAC | Archived | 0000014101 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Check airflow and flush coils when necessary. | 03/04/2024 09:20:00 AM | 3/4/24- AB1- traced air duct back to manual air volume adjust, it was open. Flushed coils in 101, and 103. | 03/04/2024 09:29:00 AM | General Maintenance
HVAC | Archived | 0000012257 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | took temps 30 mins apart reading no higher than 65/67 degress in all 3 rooms | 02/22/2024 10:29:00 AM | 2/21/24- AB1- Pulled strainer in 102 and flushed system. 2/23/24- AB1-Pulled strainers for remaining TUs in this zone. And flushed coils. Identified that there is an air flow issue that still needs to be addressed 2/28/24- AB1- Checked temperatures. Okay at this time. | 02/28/2024 02:08:00 PM | General Maintenance
HVAC | Archived | 0000011968 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | came in this morning took temp cafe was reading 60 degrees around 615am / took another temp at 810 am reading 62 degrees | 02/16/2024 09:20:00 AM | 2/15/24- Identified problem, removed motor assembly for replacement, removed moto from assembly and cleaned up remaining components in preparation for new motor. 2/16/24- Installed motor, and capacitor to motor assembly. Installed motor assembly in unit. Tested operation. | 02/27/2024 02:16:00 PM | General Maintenance
HVAC | Archived | 0000011781 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | No air volume control, just blasting full volume of air from RTUNW (Andrew put your parts on work order) | 02/13/2024 12:58:00 PM | 2/7/24-AB1 discovered that volume controller was not working correctly, and also discovered that damper shaft was broken and not allowing any control of airflow. Removed broken damper. 2/8/24- AB1 attempted to fit damper back into unit but not able to get seated in place. Need to modify shaft length to fit. Flushed heating coil to maximize flow. 2/12/24- AB1 installed damper 2/13/24 -Replaced volume control, and actuator 2/28/24-AB1- Had Tom put parts on ticket. | 02/13/2024 07:04:00 AM | General Maintenance
HVAC | Archived | 0000011670 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | BOILER PM AND SAFETY DEVICE EXERCISE. | 02/12/2024 12:15:00 PM | 2/12/2024.(RM-2). Check boiler for water leaks, check current operating pressure @ 30 PSI, check building pump operation, check circulator pump operation, check the burner control sequence of operation, check the combustion damper operation, flush the LWCO, flush the SRV, exercise the safety devices, check the email alert response, check the log sheet, monitor operation.Fill out Asset Essentials. | 02/12/2024 09:21:00 AM | Boiler
HVAC | Assigned | 0000020103 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Need holes replace have part asking to get install , Part located in Custodial office | 05/03/2024 02:36:00 PM |  |  | General Maintenance
HVAC

## 2023 PM HTG Work Orders
WOID | Description | Status | Craft | Location | Request Date | Actual Completion Date | Action Taken | Purpose
270793 | Monthly - FILTER 1'-BWES-QUARTERLY - Refer to PM schedule details. | Closed Work Orders | Filters | Bryant Woods ES | 2023-02-01 04:24 | 2023-02-06 | Changed the 1'' filter in the kitchen | Preventive Maintenance
273940 | Monthly - FILTER 2' MERV 13-BWES-SEMI - Refer to PM schedule details. | Closed Work Orders | Filters | Bryant Woods ES | 2023-03-01 04:51 | 2023-03-29 | Walked the school because the google sheet didnt look accurate. I was right for thinking that because there was 7 units that were recorded wrong. (theres no 2'' Merv 13 filters here) | Preventive Maintenance
277826 | Monthly - FILTER 1'-BWES-QUARTERLY - Refer to PM schedule details. | Closed Work Orders | Filters | Bryant Woods ES | 2023-04-01 04:45 | 2023-05-15 | BH-1 Tuesday 5-9-23 Pulled and replaced filters | Preventive Maintenance
288935 | Monthly - FILTER 1'-BWES-QUARTERLY - Refer to PM schedule details. | Closed Work Orders | Filters | Bryant Woods ES | 2023-07-01 03:44 | 2023-07-19 | BH-1 Wednesday 7-19-23 Inspected CUH's and found unit not running during summer months. Filters in units look good and does not need replacing at this time. No further issues found. | Preventive Maintenance
289034 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-07-01 03:45 | 2023-09-14 | *Need to check air pressure on actuator and guarantee it has adequate air to open fully, also check both refrigerant circuit pressures to figure out why both need to be running with cooling command. 8/10/23-AB1 & CB2 checked cooling and heating operation. Tightened any lose wiring connections. Checked amps on all motors, coils, filters, dampers, and looked for evidence of refrigerant leakage. Noticed the GOT2 was jumped out with both Compressors energized, also notice that the mechanical cooling lockout was jumped out keeping the unit from truly operating in economization mode. Found that the reason for this is because the OA Damper actuator is not stroking out far enough to make the end end switch. | Preventive Maintenance
289037 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-07-01 03:45 | 2023-08-15 | *Repair needed, COMP 2 needs to be Replaced, Economizer damper not opening fully and keeping end switch for power exhaust from making* 8/3/23-AB1 Inspected electrical, belts, pulleys, coils and dampers. Cleaned dust and debris and lubricated all parts that accept lubricant. Noticed oil around Comp 1 Suction line Rotalock Fitting, removed insulation and cleaned thoroughly to inspect better for Refrigerant leaks. Economizer damper not fully open and keeping end switch (S1) for power exhaust from making. C2 one will not run due to open internal overload. | Preventive Maintenance
289039 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-07-01 03:45 | 2023-08-15 | *Repair needed, COMP 1 Open Windings, needs to be replaced. Condenser coil needs to be cleaned. Economizer damper not opening fully and keeping end switch for power exhaust from making* 8/3/23-AB1 Inspected electrical, belts, pulleys, coils and dampers. Cleaned dust and debris and lubricated all parts that accept lubricant. SF belt over tightened causing premature bearing wear. Loosened belt and greased motor bearings. Economizer damper not fully open and keeping end switch (S1) for power exhaust from making. C1 one will not run due to open windings C2 sight glass showing good bit of bubbles most likely because of how dirty the condenser is. Notice burnt wires on condenser fan contactor due to lose spade connectors- repaired connections. | Preventive Maintenance
289040 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Declined | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-07-01 03:45 |  | Technician did not have time | Preventive Maintenance
289038 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Declined | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-07-01 03:45 |  | Technician did not have time | Preventive Maintenance
289035 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Declined | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-07-01 03:45 |  | Hvac technician did not have time for PM | Preventive Maintenance
289036 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Declined | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-07-01 03:45 |  | Hvac technician did not have time for PM | Preventive Maintenance
289041 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-07-01 03:45 | 2023-09-14 | 8/08/23-Check overall operation of unit and tightened wires. | Preventive Maintenance
289042 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Declined | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-07-01 03:45 |  | Hvac technician did not have time for PM | Preventive Maintenance
289229 | Yearly - PORTABLE TEMP-BWES-SUMMER - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-07-01 03:46 | 2023-07-12 | Set Cooling setpoint to 82 Degrees. Set Fan to AUTO. Except for: 258 is storing musical equipment and I set the thermostat to 76 and set the fan to auto. | Preventive Maintenance
294089 | Yearly - PORTABLE TEMP-BWES-WINTER - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-08-12 00:26 | 2023-08-29 | 8/16/23 AB1 Set all portables to 74 degrees and Fan AUTO | Preventive Maintenance
297642 | Yearly - Filter 2' Merv 8,4'&12'-TSES-Yearly - Refer to PM schedule details. | Closed Work Orders | Filters | Bryant Woods ES | 2023-09-01 | 2023-09-12 | BH-1 Friday 9-1-23 Pulled filters needed per Google sheet. With the help of Justin. G and AJ filters were pulled up onto roof top. All filters were replaced found some filters missing from Google sheet. Left and picked those filters up as well. Took all old filters that were removed to the dump for disposal. Pics of coils, old filters and new filters have been provided below. | Preventive Maintenance
301532 | Monthly - FILTER 1-in. (Merv 8)-BWES-QUARTERLY - Refer to PM schedule details. | Closed Work Orders | Filters | Bryant Woods ES | 2023-10-01 03:41 | 2023-10-16 | BH-1 Thursday 10-12-23 Pulled filters needed for replacement. Replaced indoor 1 inch filters and all portable unit 1 inch filters. | Preventive Maintenance

## 2023 NON PM HTG Work Orders
WOID | Description | Status | Craft | Location | Request Date | Actual Completion Date | Action Taken | Purpose
268010 | Temp. reading 65 degrees | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-01-03 | 2023-01-09 | checked space temp and space temp 68 degrees. supply air to classroom 82 degrees. | General Maintenance
270904 | Temp. reading 64 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-02-01 | 2023-02-03 | inspected room and found temp ranging between 66-67 degrees. no heat from vav box. inspected and found stat not regulating pressure. replaced stat. calibrated and tested. vav now discharging 85 degree air and space warming. | General Maintenance
271132 | check oa dampers | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-02-03 | 2023-02-03 | inspected oa dampers and made sure they all close catch up on paperwork | General Maintenance
271498 | Panasonic interverter timer is flashing red in the server room (media work room) the room is hot. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-02-07 | 2023-03-13 | 2/15/23: investigated and found unit not running. reset and unit came on. only ran for a little and shut off. possible low charge. will return to check outdoor unit. (other tech tested for me and found low on charge. they were unable to charge due to weather conditions. i will return to charge) 3/1/23: went to charge system but storm arrived. will return to charge. 3/2/23: went to supply house and picked up r410 a. returned and found oil around outdoor connection. re-sealed. pressure tested and evacuated system. charged up. discharging 53 degree air at indoor unit. cleaned condensor coil. | General Maintenance
271934 | Temp. reading in back pod area. 60 - 65 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-02-13 | 2023-02-23 | found freeze stat tripped for rtu sw. reset and tested. working normally. spaces heating up. caught up on paperwork | General Maintenance
272338 | burning like smell in room 129 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-02-16 | 2023-02-23 | checked location and found smell was from gas heat. gas heat hasnt run in a while and smell was heat exchanger. opened economizer to allow smell to dissipate. will return in the am to run heat and remove smell. 2/17/23: returned and ran gas heat for 30 minutes and opened economizer to allow space temps to settle. no more smell from rtu heat. | General Maintenance
272668 | Temp. reading 59 in cafeteria. | Duplicate Request | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-02-21 |  | repair work on ticket 272812 | General Maintenance
275303 | RTKA-Art and RTGY-Gym Units in alarms. Supply fan status. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-03-10 | 2023-03-10 13:31 | Check both and both were still running. Supply Fan Command: On, Supply Fan Status: On(*Alarm*). Reset unit disconnect to reset the board. | General Maintenance
276741 | Panasonic HVAC unit is not working in the media server room. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-03-23 | 2023-10-30 | **Replaced on 10/20/23 see ticket 298101 Indoor unit not running with flashing red light saying "timer." Power failed and restored power to reset. Checked outdoor for temp differential across lineset. No differential, need to check charge. 6/1/23- AB1- Checked charge found completed flat. Charged with nitrogen to pressure test. Pressure steadily dropped. Found leak on flare connections at outdoor and also found a leak on line set just before the indoor coil; Because of the location of the leak on line set on evaporator and the diteriation of the copper the indoor unit need to be replaced. Will replace full system during summer. 10/2/23 Due to lots of other high priority tickets we were not able to get this unit replaced this summer. Will be talking to shop lead to plan replacement. 10/20/23- Finished see ticket 298101 for documentation. | General Maintenance
277474 | 105, and 132- I was informed by day-chief that both of these rooms were warm. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-03-30 | 2023-04-12 13:41 | Took temperature in both rooms and both were above set point. In 105 I found the airline that connected to the valve actuator split and popped off. Trimmed line and re-connected. Checked discharge temp to prove that its cooling. In 132, thermostat was set to 76 degrees. Set down to 72. Will check temperatures tomorrow before closing work order. | General Maintenance
279027 | air has stopped working | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-04-13 | 2023-04-28 | Breaker turned off, spoke with Principle about findings | General Maintenance
284221 | 83 degrees in media sever room, leaving the door open it get to warm closing it. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-05-26 | 2023-06-05 13:30 | See: 276741 for labor and progress detail | General Maintenance
285963 | Exhaust fans in gym not working | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-06-06 | 2023-09-20 | Found teacher had the breaker for the gym unit off again. EF are interlocked with the gym unit. EF-1 has a bad motor, and EF-2 didnt have pully installed with keyway and the pully came loose. Blower shaft damage and motor likely on its last leg. Completed See Ticket number: 298101 | General Maintenance
286557 | Portable 257 is hot heat is blowing (85 degrees) | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-06-12 | 2023-06-14 | Found Unit Running but with signs of low refrigerant. Checked pressure and it turned out the the unit needed to be charged. Removed remaining refrigerant, vacuumed system, and then charged with 4.5lbs of R410A . Please charge out the Refrigerant on your service ticket. | General Maintenance
287467 | No air conditioning in the building | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-06-20 | 2023-06-21 | 6/21/23- AB1- Spoke with Maderia, and let her know about summer time operation and that only the Office unit is scheduled to run during the summer unless a request is made to EMS for a scheduled assembly, work that requires cooling, sporting event, or summer classes. A request will need to be made by Thursday of the week prior to the week of the event, if a specific zone needs cooling for any of the above reasons. We did however find that the front office unit had a occupancy scheduling error that needed to be correct. Called Tom O. to correct schedule for Office unit. | General Maintenance
288376 | Request for air on 7\3,5,6,7 for 128 - 132 to do carpets. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-06-29 | 2023-06-30 | Scheduled | General Maintenance
294974 | Room is extremely warm and stuffy no air seems to be on. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-08-18 | 2023-09-20 | 8/21/23 Needs a new volume controller. Manually set damper to mid position to allow for some cooling. Also unit discharging higher than normal temp need to investigate. *Completed See Ticket# 298101* | General Maintenance
295284 | loud ringing coming from Temperature control box in front office | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-08-21 | 2023-08-24 | 8/24/2023- Went to shop to pick up new thermostat, andCB-2 and AB-1 installed in office. | General Maintenance
295435 | temprature reads 86 degrees...... | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-08-21 | 2023-09-05 | 8/25/23-AB1- Checked operation and found that unit was going off on low pressure switch. Checked pressure, and found that unit was low on refrigerant. Recovered 1.2 lbs of refrigerant from unit. Checked for leaks with nitrogen up to 450 psi. No leaks. Proceeded evacuation. I was able to pull down to 450 microns and it help. Weighed in refrigerant charge and tested operation. All is well. Forget to add refrigerant to your work ticket please put on the ticket. | General Maintenance
295666 | 78 degrees in the portable | Duplicate Request | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-08-23 |  | See: 295435 | General Maintenance
296367 | Temp. reading 80 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-08-28 | 2023-09-20 | 8/29/23-AB1 Found problem VAV Volume controller- Not opening up to allow box flow. Manually adjusted damper to 30% position to provide constant volume of cool air. Also found problem with RTUNW not discharging bellow 67 degrees. Filters need to be changed. Outdoor air fully open and return air shut. Stage 1 cooling not working because wires were removed from GOT. disconnected linkage and set in a min position, and removed dirty filters. Brought discharge temp down to 59. 8/30/233-AB1-Checked RTUNW EP for problems. No problem found. Did find that min position relay sending to high of a volume of air to damper. Set down to 10% min. Checked RTUNW Stage 1- found bad compressor. Will need to replaced. Completed original concern, but will be documenting compressor change on 298101. | General Maintenance
296457 | Temp. reading 79 | New Request | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-08-28 |  | 8/29/23- Checked temp, looked for VAV in ceiling. It looks like the VAV is actually in a neighboring room. Repairing RTUNW helped bring temp down to could guidelines 8/30/23- Checked temp, still seems a little warmer then neighboring rooms with not much air flow. | General Maintenance
298101 | RM 105, 127, 128, 129, 130, 137, 139, 141(gym) all have very hot temps inside | Work In Progress | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-09-05 |  | 10/9/23- cleaned strainers and flushed coils in rm 117, and rm 110, and rm130. Checked bypass dampers on RTUNE, RTUNW, RTUSE, RTUSW, and RTUKA. Discovered issue with economizer function on RTUNE, overoad to OFF and set to run mechanical cooling. 10/11/23- AB1 & CB2 discovered that the mixed air damper was getting supply air pressure from a the Min Position relay (set to 10psi) adjusted to 15psi economizer works ON/OFF through bas. Still need to address issue with controls team to still have minimum position. Worked with Frank L on addressing control issue. Added a EPC(Override Gage) to control system in order to contol ECON and Min position. Tested operation. EPC works fine but actuator was getting hung up. need to replace actuator. Installed EVAP wall unit, connected copper tubing, and wired. 10/12/23-AB1&CB2 Replaced actuator on RTUNE and tested with Frank L. Met Reedy Electrical for workroom unit power check, they disconnected power to make it safe for demo. Finished piping for MDF room(soldering a 45 fitting was required), cleaned up line-set, wire run, and work area. Re-installed ceiling tiles. Troubleshooting of Computer lab ceiling cassette ductless unit- Flat on charge, put nitrogen holding charge of 200psi. 10/17/23 mg1 assisting with compressor lift & installation 10/26-Met Wayne from electrical shop to assist with electrical disconnect hook up for workroom and server room ductless units. Assisted Dennis with work downstairs. Followed up with Larson about completed work. Troubleshot RTUNW and found that C1 needs a new TXV. 10/30/23-Checked temps throughout building, noted cold spots, flushed room 102 coil, several buckets full that were still black, got some flow though but needed to wrap up for the day. 10/31/23- Worked with DS on RTUSW unit econ function. Was not economizing, needed to reroute airlines to supply minimum position air and econ air. Flushed room 102 coil, removed lots of sediment, took 6 buckets for water to start clearing. | General Maintenance
299045 | media return (in ceiling) needs to be vacuumed or removed and cleaned | New Request | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-09-11 |  |  | General Maintenance
299615 | calibrate volume controller | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-09-14 | 2023-09-14 | calibrated volume controller for rtu nw for better discharge air temps and adjusted oa dampers to a minimum position | General Maintenance
300441 | HVAC/BAS shop Plans to upgrade controls at the school. Controls work will be done in-house, requesting proposals from contractors for blower motors and VFD's. | Work In Progress | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-09-22 |  | Ordered 8 CGM controllers from JCI for the project, see attached. VFD's and blower motors awarded to Easi, see attached. | General Maintenance
302828 | trained and aided in replacing txv | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-10-10 | 2023-10-10 | aided in training and replacing txv. building tech making replacement ticket | General Maintenance
303003 | Units not controlling Econ, OA damper fully closed per Andrew. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-10-11 | 2023-10-16 | 10/11/23: Went to Bryant woods after that, RTNE not controlling the Econ dampers properly per Andrew, looked into the pnuematic set up, no OA lockout relay available on this unit like the others, decided to Add a new EPC and allow the controller tell the damper what to do, went to the shop and got a new EPC, installed, pulled program, added mixed air damper outpu to it, downloaded, tested and verified proper operation with Andrew on the roof Damper actuator is not holding steady, told him to take a pic so we can order new, have the actuator at the shop, will return to replace and finalize. Actuator replaced by Andrew, tested and verified all with him in the field. | General Maintenance
303806 | inspect oa damper per LA | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2023-10-19 | 2023-10-19 | inspected OA damper on portable 234 and made sure it opened whenever fan operates. left to inspect another portable. returned and set stat to fan ON position her email I received. | General Maintenance
0000001062 | BOILER PM AND SAFETY DEVICE EXERCISE. | Archived | HVAC | Bryant Woods ES | 11/02/2023 | 11/06/2023 | 11/2//2023. (RM-2). Check boiler for water leaks, check current operating pressure @ 30 PSI, check building pump operation, check circulator pump operation, check the burner control sequence of operation, check the combustion damper operation, flush the LWCO, flush the SRV, exercise the safety devices, check the text alert response, check the log sheet, monitor operation | General Maintenance
0000004644 | Josh R. inform me a of Status alarm on RTAKA. | Archived | HVAC | Bryant Woods ES | 11/28/2023 | 2023-11-28 | 11/28/23- AB1- Talked to Josh R. for info. RTUKA as well as RTUNW unit status alarm. Reset both controllers to resolve. Verified proper operation. RTUNW status still in an alarm state on metasys but no trouble found in actual operation. | General Maintenance
0000004277 | meet contractor | Archived | HVAC | Bryant Woods ES | 11/22/2023 | 2023-11-22 | 11/22/23- met contractor | General Maintenance
0000004186 | BOILER PM AND SAFETY DEVICE EXERCISE. | Archived | HVAC | Bryant Woods ES | 11/21/2023 | 2023-11-21 | . 11/21/2023.(RM-2). Check boiler for water leaks, check current operating pressure @ 30 PSI, check building pump operation, check circulator pump operation, check the burner control sequence of operation, check the combustion damper operation, flush the LWCO, flush the SRV, exercise the safety devices, check the email alert response, check the log sheet, monitor operation. | General Maintenance
0000004185 | EMERGENCY PREPAREDNESS. | Archived | HVAC | Bryant Woods ES | 11/21/2023 | 2023-11-21 | 11/21/2023.(RM-2). Informed those present of the location, purpose and funtion of the emergency power off switches by the exit doors that serve the heating water boiler. | General Maintenance
0000002345 | Took temp 9:00 am portable holding cold temps 51-52 degrees | Archived | HVAC | Bryant Woods ES | 11/06/2023 | 2023-11-06 | 11/6/23-AB1, Found unit off, opened up bard unit control cabinet. Checked for 24V control signal on transformer. No 24V= Bad transformer, need to replace with a overload switch to diagnose low voltage short or back feed. Will return soon. 11/9/23-AB1, Replaced transformer and tightened all wire connections, tested for shorts to ground, and tested in various operating settings. No problems at this time. Unit heats and cools now. | General Maintenance
0000001207 | took a temp with senor reading 44 degress very cold need fix soon as possible thanks | Denied | HVAC | Bryant Woods ES | 11/03/2023 | 2023-11-03 | See ticket number 2345, this is a duplicate request. | General Maintenance

## 2022 PM HTG Work Orders
WOID | Description | Status | Craft | Location | Request Date | Actual Completion Date | Action Taken | Purpose
221562 | Yearly - AIR COMPRESSOR-BWES-YEARLY - Refer to PM schedule details. | Declined | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-02-01 04:18 |  | Changed the status from on hold to declined due to being Sept 22 and the next frequency will be Oct 1st. | Preventive Maintenance
221702 | Yearly - Belt Change-Bryant Woods ES-Yearly - Refer to PM schedule details. | Closed Work Orders | Filters | Bryant Woods ES | 2022-02-01 04:20 | 2022-03-08 | Pulled belts delivered to school. Started belt change n greasing motors n bearings. Completed belt change n greasing motors n bearings in all units n ex-fans. | Preventive Maintenance
222121 | Monthly - FILTER 2' MERV 13-BWES-SEMI - Refer to PM schedule details. | Closed Work Orders | Filters | Bryant Woods ES | 2022-02-01 04:24 | 2022-03-08 | Pulled Filters from ARL and Wilde Lake high complete filter order to start filter change. Completed filter change n all rooftop units and cleaned off of all balls and all the used filters. | Preventive Maintenance
225267 | Yearly - DX OFFICE UNIT-BRYANT WOODS-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-03-01 11:05 | 2022-03-24 | performed pm on unit. made sure components work. found leaking ep in control cabinet. replaced. found issue with dx cooling control signal. too cold to troubleshoot now. will return to troubleshoot on warmer day. | Preventive Maintenance
225362 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-03-01 11:06 | 2022-06-08 11:19 | Yearly preventive maintenance | Preventive Maintenance
225363 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-03-01 11:06 | 2022-06-08 11:19 | Yearly pm | Preventive Maintenance
225364 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-03-01 11:06 | 2022-06-08 11:19 | Yearly pm | Preventive Maintenance
225365 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-03-01 11:06 | 2022-06-17 | Yearly pm | Preventive Maintenance
225366 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-03-01 11:06 | 2022-06-08 11:20 | Yearly Preventive maintenance | Preventive Maintenance
225367 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-03-01 11:06 | 2022-06-08 11:19 | Yearly Preventive maintenance | Preventive Maintenance
230058 | Monthly - FILTER 1'-BWES-QUARTERLY - Refer to PM schedule details. | Closed Work Orders | Filters | Bryant Woods ES | 2022-04-01 04:30 | 2022-04-25 | Completed filter change. | Preventive Maintenance
242957 | Monthly - FILTER 1'-BWES-QUARTERLY - Refer to PM schedule details. | Closed Work Orders | Filters | Bryant Woods ES | 2022-07-01 05:01 | 2022-07-18 | changed the 1'' filter | Preventive Maintenance
243055 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-07-01 05:02 | 2022-07-13 | pm unit | Preventive Maintenance
243056 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-07-01 05:02 | 2022-07-14 | pm unit | Preventive Maintenance
243057 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-07-01 05:02 | 2022-07-15 | perform pm | Preventive Maintenance
243058 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-07-01 05:02 | 2022-07-28 | perform pm on unit | Preventive Maintenance
243059 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-07-01 05:02 | 2022-07-28 | perform pm | Preventive Maintenance
243060 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-07-01 05:02 | 2022-07-26 | perform pm | Preventive Maintenance
243061 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-07-01 05:02 | 2022-07-13 | pm unit | Preventive Maintenance
243062 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-07-01 05:02 | 2022-07-13 | pm unit 8/11/22: recovered charge from unit and disconnected all electrical for compressor replacement. 8/12/22: picked up parts at supply house for replacement 8/19/22: picked up parts from supply house and added to ticket 8/22/22; unbrazed compressor and sealed for replacement 8/23/22: removed compressor from building with crane. installed compressor and parts. pressure tested and evacuated. added 422B to system. added acid treatment. will return to check on acid in system. | Preventive Maintenance
243063 | Yearly - HVAC SUMMER PM-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-07-01 05:02 | 2022-07-13 | perform pm on unit | Preventive Maintenance
246869 | Monthly - FILTER 2' MERV 13-BWES-SEMI - Refer to PM schedule details. | Closed Work Orders | Filters | Bryant Woods ES | 2022-08-01 06:16 | 2022-08-24 | Walked Roof Top and recorded all Filter sizes in roof Top units. No Merv 13 filters at school . Filters are 4 inch and Merv 8 only. | Preventive Maintenance
248749 | Confirmation of Proper OA Damper and Exhaust Fan Operation. Record the results of your confirmation of proper outdoor air damper and exhaust fan operation in the Google Forms. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-08-12 | 2022-08-16 | 8/15/22: checked all unit dampers and exhaust fans. all dampers bringing in OA and fans running. | Preventive Maintenance
251955 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-09-01 05:11 | 2023-02-21 | Visual Inspection, Filter Changed, and Test in Heat and Cool. | Preventive Maintenance
251956 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-09-01 05:11 | 2023-02-21 | Visual Inspection, Filter Changed, Tightened Wire and Tested Heat and Cool | Preventive Maintenance
251957 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-09-01 05:11 | 2023-02-22 | Visual Inspection, Filter Changed, and Heat and Cool Operation Check | Preventive Maintenance
251958 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-09-01 05:11 | 2023-02-21 | Visual Inspection, Filter Change, and Test Heat and Cool Operation | Preventive Maintenance
251959 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-09-01 05:11 | 2023-02-22 | Visual Inspection, Filter Change, and Test Heat and Cool | Preventive Maintenance
251960 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-09-01 05:11 | 2023-02-22 | Visual Inspection, Filter Changed, and Heat and Cool Operation Check | Preventive Maintenance
256305 | Yearly - AIR COMPRESSOR-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-10-01 05:00 | 2022-11-03 | Was able to change the Oil, belts, Air- filter, and greased the bearings on the motors on the Air- Compressor. Also was able to go to RHHS to get the information off of the Air- Compressor there. | Preventive Maintenance
260466 | Monthly - FILTER 1'-BWES-QUARTERLY - Refer to PM schedule details. | Closed Work Orders | Filters | Bryant Woods ES | 2022-11-01 04:30 | 2022-11-07 | Pulled the one filter needed for this school's 1'' filter change but it was wrong so i had to go back to ARL and get the right filter. Then i came back and changed it. | Preventive Maintenance
261094 | Yearly - CAN WASH-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-11-06 01:46 | 2022-11-21 | tested heater working normally | Preventive Maintenance
261161 | Yearly - MECH RM HTR-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-11-06 01:48 | 2022-11-21 | tested heater working normally | Preventive Maintenance
264998 | Yearly - Belt Change-Bryant Woods ES-Yearly - Refer to PM schedule details. | Closed Work Orders | Filters | Bryant Woods ES | 2022-12-07 01:11 | 2023-02-10 | Changed all belts in the units and greased all bearings. Just need to do a few exhaust fans. Changed the rest of the exhaust belts but on EF-2 the motor/shaft is frozen up. | Preventive Maintenance

## 2022 NON PM HTG Work Orders
WOID | Description | Status | Craft | Location | Request Date | Actual Completion Date | Action Taken | Purpose
219786 | Media temp. reading at 60 degrees | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-01-11 | 2022-01-19 | DS-2 1/14/22 Checked temp on computer, its was 66 but units just came on. Looking at history the past 2 days it was 68 to 69 in space. I'll check temps later today again. | General Maintenance
219895 | Temp. reading 64 degrees in room 129 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-01-12 | 2022-01-12 | Checked classroom temp was reading 65 adjusted stat to 71 temp checked temp before leaving room was reading 70 | General Maintenance
221357 | No heat in portable 234 temp. reading 39 and wall thermostat reading 43 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-01-28 | 2022-02-15 | 1/28/22- Received service call and traveled to site. Signed in with the front office. P234 room temperature to be 48F with the heat calling. Inspected unit. Identified the supply side power wires to the heating contactor as burnt through. Heating contactor was also damaged. Unwired and removed heating contactor. Secured new 2pole 40FLA contactor in place. Removed damaged portions of wiring and connectors. Landed all wiring on the contractor. Tested system. System working appropriately at this time. Stood by to allow portable to reach room temperature setpoint. Service complete. | General Maintenance
222495 | No heat in room 129 temp. reading 62 degrees | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-02-03 | 2022-02-04 | Inspected the area Classroom was 68 degrees adjusted temp two degrees room Began to warm will check tomorrow 2/3/22 Followed up on classroom room is working normal operation temp 72 deg F 2/4/22 | General Maintenance
222801 | Portable 113 no heat temp. reading 36 wall thermostat reading 38 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-02-07 | 2022-02-22 | Emay will write there service ticket and I will close this ticket. | General Maintenance
223493 | High pitch buzz coming from thermostat box on wall in front office | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-02-14 | 2022-02-18 | Checked and found bad thermostat.Replaced stat and set temp setpoint to70deg.Checked operation.Will have Bld tech check stat and calibrate if needed. JR2 2/14/22: verified calibration of stat. | General Maintenance
224340 | cold in space | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-02-22 | 2022-02-22 | 2/14/22:found cafeteria temp 62 degrees. low discharge air temp. building had lost power over weekend and unit was checked out by on call tech. inspected unit and made sure nothing was tripped. blower running. heat pe switch not calling. adjusted volume controller and heat came on. monitored and had to adjust a few times to get correct temp in cafeteria. | General Maintenance
224342 | cold in space | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-02-22 | 2022-03-04 | 2/14/22: inspected space and found space temp 66 degrees. inspected rooftop unit and found heat running. looks like only low fire running. will get new heat control board for unit. 2/15/22: picked up new board for unit. 3/4/22: dropped off boards to boiler room cabinet. will swap out old boards when summer pm starts | General Maintenance
224631 | Temp reading 63 in office area 133 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-02-24 | 2022-02-28 | Inspected room temperature was reading 71 in space | General Maintenance
224692 | Temp. reading in cafeteria 60 degrees | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-02-25 | 2022-02-28 | Inspected cafeteria temperature was reading 60 degrees. Adjusted receiver controller causing gas heat to cut on. temp reading 70 degrees Cafeteria now heating | General Maintenance
224703 | Thermostat in front office is making a whistling sound | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-02-25 | 2022-02-28 | Thermostat out of calibration.Re-calibrated thermostat and set temperature back to 70 | General Maintenance
224765 | Temp reading 77 degrees in room 105 (to hot) | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-02-25 | 2022-03-08 | Thermostat out of calibration, recalibrate and set to 72 | General Maintenance
228253 | Cold | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-03-17 | 2022-03-17 | Inspected cafeteria temperature was reading 65 degrees.Adjusted receiver controller so heat would cut on | General Maintenance
228442 | All portables extremely warm need to switch to air conditioning. One is reading 84 degrees. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-03-18 | 2022-03-22 | Inspected all portables, all stats set to fan on. Changed all stats to auto and asked teachers to please close windows with windows open heat will keep running until satisfied . Found two portables with windows left open spoke to Front office secretary and let her know of issue. Systems now working in normal operation | General Maintenance
228347 | Temperature @ 62 degrees. Please make adjustments Time Available: asap | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-03-18 | 2022-03-23 | 3/22/22: checked unit and found heat running. Inspected RTU and controls. All working. Will return in the am to check. 3/23/22: returned at 715am and RTU no discharging 118 degree air. Space temp 69 degrees. Will monitor. Working normally right now. | General Maintenance
228999 | gym warm | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-03-24 | 2022-03-24 | 3/23/22: found gym over heating. air leak in heating cabinet. repaired air leak. had to adjust receiver controller a few times to get proper heat cycle temps. working normally. gym temp 69 degrees. | General Maintenance
229240 | temperature @ 48 degrees please adjust to a warmer temp. Thank You Time Available: asap | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-03-28 | 2022-03-30 | 3/28/22: checked and found receiver controller not regulating pressure. nite stat also not working properly. ordered new night stat and adjusted controller so that heat running. spoke with controls department about running heat off of space temp instead of pneumatic signal. they liked idea and will reprogram when their project is done. 3/29/22: checked and unit heating space. | General Maintenance
229554 | 63 degrees in cafeteria. please make it warmer. thanks Time Available: asap | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-03-30 | 2022-03-31 | adjusted Receiver controller 8psi , system issue will be worked on by Frank | General Maintenance
229642 | Unit not running | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-03-31 | 2022-04-05 | Unit tripped from freeze stat reset stat system up and running | General Maintenance
230229 | gym warm | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-04-01 | 2022-04-01 | found receiver controller not working again. adjusted and gym cooling down. spoke with Frank L this morning about removing pneumatic controllers for gym and cafe and controlling them through bas. meeting at location next week to do a site survey. 4/4/22: checked space after weekend. made sure heat cycled on to heat space. | General Maintenance
231097 | Temp. reading 80 in room 105 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-04-08 | 2022-04-11 | Inspected classroom temp was set for 72 and classroom was 72 did not find any issue | General Maintenance
231981 | 45 degrees in portable 4 #204 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-04-19 | 2022-04-27 | JR-2 4/21/22: got a call from portable tech to help diagnose unit. fan wont run. checked relay components and all working. capacitor checked out ok. 4.9mfs. will return to finish diagnosis in the am. 4/22/22: returned and finished checking out motor. hooked motor up to tb and still not running. called lange and went and picked up new motor. returned and installed motor. motor rotation backwards. will return mon morning to swap around. 4/25/22: returned and removed motor assembly and swapped motor. re-installed motor assembly. placed in heat mode. fan came on and so did electric heat. unit discharging 95 degree air and heating space. | General Maintenance
233230 | Document Model/Serial Number of Minisplit FCUS on Google form | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-04-29 | 2022-04-29 10:29 | 4/28/22-AB1-Document Model/Serial Number of Minisplit FCUS on Google form | General Maintenance
235784 | install thermostat signs | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-05-16 | 2022-05-16 | install signs above thermostat and check settings. | General Maintenance
236284 | 128 - 132 is reading 82 - 84 degrees to hot | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-05-20 | 2022-06-23 | 5/20/22: found rtu sw cooling command on. discharge air reading 85 degrees. went to school and checked cooling pe. calling for cooling. inspected rooftop unit and found bad compressor contactor for compressor 1. jumped out compressor 2 to run. space cooling. will return 5/23 am to replace contactor. 5/23/22: get model # for havtech 5/25/22: picked up parts 6/10/22: had testing in space. didnt want to shut unit down for repair. will return 6/13/22 6/17/22: shut down unit. removed and replaced old contactor. reconnected low voltage and started up. contactor now sending 3 phase power to compressor but compressor not running. windings not open. compressor bad. will order when money in budget. re-hooked up so 2nd stage runs. unit cooling with 2nd stage. | General Maintenance
238472 | 136 - 140 temp. reading 80 -82 (137 is special needs students) | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-06-02 | 2022-06-03 | 6/3/22: checked and found rtu se discharge air 54 degrees. space temps between 71-74 degrees. OA temp 76 degrees. will monitor when OA temps get hot again. | General Maintenance
240186 | gym unit not running | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-06-15 | 2022-06-15 | 6/13/22: found gym unit not running on BAS. arrived and inspected. found no power to unit. breaker turned off. turned on breaker and unit running normally. exhaust fan running. gym teacher must have turned breaker off. will let him know when i see him to leave on due to COVID protocols. | General Maintenance
240676 | Ensure that the thermostats are set to 76°F and the fan speed switches are set to the “Auto” position. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-06-21 | 2022-06-23 | 6/22/22: changed settings to unit per hvac dept email | General Maintenance
241539 | rtu gym in alarm | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-06-23 | 2022-06-23 | 6/22/22: found rtu gym in alarm on bas. inspected unit and found fan not running. no power at unit. no power to disconnect. checked breaker in gym storage and found turned off. turned on and unit came on. running normally. also gym exhaust fans were left in hand. probably both issues caused by gym teacher. placed fan back in auto. | General Maintenance
243750 | Ensure that the thermostats are set to 82°F and the fan speed switches are set to the “Auto” position. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-07-07 | 2022-07-11 | changed stats to 82 degrees | General Maintenance
248223 | There is no air in the back half of the building (110 -134) | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-08-09 | 2022-08-10 | units are not scheduled to run in the back of building. | General Maintenance
248512 | Can I have the air conditioning on till 9:30pm tomorrow in classrooms 105,106,107,108,109,110,112,and 115 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-08-10 | 2022-08-11 | scheduled | General Maintenance
248546 | Need air on in the evenings to do carpets 8\11, 8\12, 8\15 -8\19 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-08-11 | 2022-08-17 | Scheduled | General Maintenance
249246 | supply fan not running | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-08-16 | 2022-08-24 | 8/11/22: found supply fan not running. found transformers tripped. reset and tripped again. looked for short. found bad coil on condenser fan contactor. will return with part. 8/23/22: replaced contactor and unit cooling normally. | General Maintenance
249887 | change temp in portables | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-08-19 | 2022-08-19 | changed temp back to normal operation | General Maintenance
250694 | Fans in gym not working | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-08-25 | 2022-08-30 | inspected gym and found grym rtu main breaker turned off and exhaust fan switch turned off. turned on breaker and placed ex fan in auto and both running. informed gym teacher that these need to remain on due to covid regulations. | General Maintenance
250700 | Back part of building hot :media 78 degrees, 128 - 132 79\80 degrees | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-08-25 | 2022-09-07 | 8/26/22: found bad compressor contactor for rtu nw. switched to stage 2 cooling. ordered new contactor and picked up from aireco. will return to replace. 8/31/22: returned and replaced contactor. power going to compressor but not running. terminals opened. will need new stage 1 compressor. informed lead man. no data plate on compressor. sent data plate infor from unit. media center receiver controller needed to be adjusted. compressor running and space temp 74 degrees. | General Maintenance
251219 | 110 & 113 79 Degrees | Duplicate Request | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-08-29 |  | waiting on a part | General Maintenance
251508 | not cooling | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-08-30 | 2022-08-30 | complaint that space is hot. found compressor running but not keeping temp. found unit low on charge. used leak detector but only could find a leak at schrader. tightened schraders. added charge. unit cooling normally. | General Maintenance
251590 | Rooms that have consistent A\C issue (like outside air blowing in) 132,139,113,111,115,131,110,123,Gym,105 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-08-31 | 2022-09-07 | found compressor 1 contactor bad in nw unit. picked up new one. replaced. found compressor windings bad. needs new compressor. building may have had power event due to many defective electrical components in different units over the last few weeks. have stage 2 compressor running. discharging 52 degree air. set receiver controllers to maintain 55 degree air. | General Maintenance
254163 | Need air to be on September 13th (Tuesday) & 14th (Wednesday) until 8 pm for back to school night. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-09-12 | 2022-09-12 | Scheduled | General Maintenance
254171 | Need air on for Back to School Night September 13th (Tuesday) & 14th (Wednesday) until 8 pm. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-09-12 | 2022-09-12 | Scheduled | General Maintenance
254478 | Gas heat control of all units are on standalone receiver controllers, go out of whack periodically, need to take full control of them. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-09-14 | 2022-09-22 | 9/13/22: Dennis went to school, Started on RTGY (Gym unit), added EPC, called me, changed the program, added the output to the controller, brought the point online for him to test, he went to the roof, started the fan and tested both stages, all worked good, RTGY is complete. 9/15/22: RTSW: Changed out the DA-T sensor of the unit, sensor bad, moved wires from EP switch, added relay for Heat enable. Tested gas operation with Dennis on the roof, did not work, see attached, corrections need to be made. RTKA: Moved wires from EP switch, added relay for gas enable, tested gas operation with Dennis on the roof, tested, all passed. RTNE: Moved wires from EP switch, added relay for gas enable, tested gas operation with Dennis on the roof, tested all passed RTSE: pulled wire for the 2 exhaust fans to lighting control panel, will terminate tomorrow, pulled wires from EP switch, added relay for gas enable, tested gas furnace with Dennis on the roof, RTNE: has relay for HTG command, HTG output in the program energizes the heat. Did not have to do anything, tested gas heat with Dennis on the roof, RTMC: Moved wires from EP switch, added relay for gas enable, tested gas operation with Dennis on the roof, RT-O (Office): pulled wires from EP switch, added relay for gas enable, added new UNT controller for both panels RT-O and RT-MP for HTG-C RT-MP (Cafe): pulled wires from EP switch, added relay for gas enable, added relay for gas enable, added new UNT controller for both panels RT-O and RT-MP for HTG 9/16/22: went back to school after Forest Ridge Gym, RTO and RT-MP: added new controller to the trunk Wired the Heating outputs of both units to the new controller, tested and verified both with Dennis. RTSE: moved EF-3&4 command to the lighting control panel controller, downloaded the controller, tested and verified their operation with Dennis. 9/19/22: Dennis went back there, called in, we tested all units with him in the field, send an email to Josh and Robb | General Maintenance
261864 | heat not working Andrew- Josh had this transferred to you 4/20/23. I took out of parts on order and made it new for you. I hope Josh told you the issue and had the part for you./ss | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-11-11 | 2023-06-16 | 11/10/22: no heat working from bas upgrade via frank l. checked and found induction motor noisey. found mounting bracket for motor broken. heat runs. will return with new motor and bracket. ordered parts through hobbs 1/6/22: picked up parts and started to remove inducer assembly. 3/30/23: AB1 installed new motor, and tested. Inducer runs but differential pressure switch wont make, need to replace diff switch. 6/6/23- Called Hobbs to check for differential pressure switch, they had it in stock but I will need to wait for approval to purchase. 6/16/23- Installed an air switch with adjustable range: .05" to 12wc and set up to only close contacts when Fan is running. | General Maintenance
261845 | Temp. reading 65 degrees in room 129 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-11-11 | 2022-11-18 | 11/11/22: checked space temps and found 67 degrees. heat coming from vav box. 82 degrees. stat set to 70 degrees. adjusted up to 72 degrees. will return to make sure space heated. most of room is outside block wall. 11/15/22: returned and space temp 73 degrees at 7am. space heating normally. | General Maintenance
262239 | 129 temp. reading 60 degrees cold | Duplicate Request | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-11-15 |  | reference wo 261845 | General Maintenance
262608 | heat not running | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-11-18 | 2023-02-23 | 11/15/22: checking out rtu-sw heat. frank l said it wasnt working during heat relay install updgrade. put unit in heat and found inducer motor runs but no heat. pressure switch broken. ordered new parts from hobbs. will return to install when arrives. 12/1/22: picked up parts for rooftop job 12/2/22: reset freezestat. will return on 12/5 am to replace roof parts. 1/17/23: returned and took all parts to roof. replaced parts for rtu sw. inducer motor wheel very dirty. removed assembly and cleaned. re-assembled and started up. tested. heat working normally. | General Maintenance
262613 | test heat | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-11-18 | 2023-02-23 | 11/15/22: checked heat from Frank L list from heat relay upgrade. found inducer motor runs and voltage getting back to ignition control but no spark. ordered new control from Havtech. will return to replace. checked shop for rtu o,se,sw parts before ordering from parts house. 2/16/23: picked up part from supply house. returned to school and installed new ignition control. tested gas heat. working normally. will return on the am to run heat and remove smell from heat exchanger. 2/17/23: ran heat to remove smell | General Maintenance
263401 | rtu sw not running | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-11-29 | 2022-11-29 | checked unit and found contactor not pulled in. has power to unit. freezestat tripped. had to locate freezestat in ductwork. reset and unit came on. classrooms heating. | General Maintenance
264471 | Portable 1 thermostat reading 70 but when I use the mini temp laser it was more like 80 degrees. (Teacher complaining) | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-12-02 | 2022-12-22 | 12/15/22: checked portable and found thermostat way out of calibration. will pick up stat and return to replace. 12/19/22: picked up stat and other parts from supply house. 12/21/22: installed new stat and programmed. running normally. | General Maintenance
264816 | Temp reading 63 degrees in rm. 102 (pre k) | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-12-06 | 2022-12-09 | checked temp on BAS. space temp 73 degrees. temp sensor in space. will monitor temp. | General Maintenance
266159 | Portable 1 temp. reading 80 wall thermostat 70 teacher having to prop door open | Duplicate Request | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2022-12-19 | 2022-12-20 | reference Work Order: 264471 | General Maintenance

## 2021 PM HTG Work Orders
WOID | Description | Status | Craft | Location | Request Date | Actual Completion Date | Action Taken | Purpose
178714 | Yearly - AIR COMPRESSOR-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-02-01 05:28 | 2021-03-17 | 3/17/21: checked new air dryer. working normally. pm'd air compressor. | Preventive Maintenance
182083 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-03-01 06:59 | 2021-09-13 | Performed annual cooling maintenance and checks. .. | Preventive Maintenance
182084 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-03-01 06:59 | 2021-09-13 | Performed annual cooling maintenance and checks. Submitted a repair request to Rob with HCPSS. .. Found blower capacitor is reading 8.8/10mfd it is failing | Preventive Maintenance
182085 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-03-01 06:59 | 2021-09-13 | Performed annual cooling maintenance and checks. Submitted a repair request to Rob with HCPSS. .. 09/09/21 Blower capacitor is reading 3.8/5mfd. Capacitor is failing. Replaced. | Preventive Maintenance
182086 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-03-01 06:59 | 2021-09-13 | Performed annual cooling maintenance and checks. .. | Preventive Maintenance
182087 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-03-01 06:59 | 2021-09-13 | Performed annual cooling maintenance and checks. .. | Preventive Maintenance
182088 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-03-01 06:59 | 2021-09-13 | Performed annual cooling maintenance and checks. .. | Preventive Maintenance
187544 | PM unit for cooling season | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-04-15 | 2021-04-28 | removed air deflectors and thoroughly cleaned condenser coils. checked condenser fan operation. lubricated blower motor and bearings. checked belt tension. placed unit into 1st and 2nd stage cooling and checked charge. sight glass full for 1st stage. distributor tubes cold. second stage low on charge. pressure tested with nitrogen. no leak found. evacuated and added charge. found off timer and contactor bad for stage 2. replaced. both stages running normally.. re-glued pvc trap. vacuumed drain pan. | Preventive Maintenance
187545 | PM unit for cooling season | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-04-15 | 2021-04-28 | removed air deflectors and thoroughly cleaned condenser coils. checked condenser fan operation. found a bad fan motor. replaced. lubricated blower motor and bearings. checked belt tension. placed unit into 1st and 2nd stage cooling and checked charge. 2nd stage empty. pressure tested with nitrogen. used leak detector and soap bubbles and couldnt find leak. put dye in system and pressure tested. found high side schrader core leaking. replaced. checked coils and copper tubes and couldnt find any other leak. evacuated system and charged 2nd stage. found bad contactor. replaced. 1st stage sight glass full. distributor tubes cold. replaced leaking schrader core from 1st stage suction fitting. 1st stage working normally. re-glued pvc trap and vacuumed drain pan. | Preventive Maintenance
187546 | PM unit for cooling season | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-04-15 | 2021-04-21 | removed air deflectors and thoroughly cleaned condenser coils. checked condenser fan operation. lubricated blower motor and bearings. checked belt tension. placed unit into 1st and 2nd stage cooling and checked charge. sight glass full. distributor tubes cold. both stages working normally. re-glued pvc trap. vacuumed drain pan. | Preventive Maintenance
187547 | PM unit for cooling season | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-04-15 | 2021-04-21 | removed air deflectors and thoroughly cleaned condenser coils. checked condenser fan operation. lubricated blower motor and bearings. checked belt tension. placed unit into 1st and 2nd stage cooling and checked charge. charge low on 2nd stage. added charge. both sight glasses full. distributor tubes cold. both stages working normally. re-glued pvc trap and vacuumed drain pan. | Preventive Maintenance
187452 | Yearly - DX OFFICE UNIT-BRYANT WOODS-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-04-15 00:58 | 2021-04-21 | removed air deflectors and thoroughly cleaned condenser coils. checked condenser fan operation. lubricated blower motor and bearings. checked belt tension. had to adjust belt. placed unit into 1st and 2nd stage cooling and checked charge. sight glass full. distributor tubes cold. both stages working normally. re-glued pvc trap. vacuumed drain pan. | Preventive Maintenance
188145 | pm unit for cooling season | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-04-21 | 2021-04-21 | removed air deflectors and thoroughly cleaned condenser coils. checked condenser fan operation. lubricated blower motor and bearings. checked belt tension. placed unit into 1st and 2nd stage cooling and checked charge. sight glass full. distributor tubes cold. both stages working normally. re-glued pvc trap and vacuumed drain pan. | Preventive Maintenance
188147 | pm unit for cooling system | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-04-21 | 2021-04-21 | removed air deflectors and thoroughly cleaned condenser coils. checked condenser fan operation. lubricated blower motor and bearings. checked belt tension. placed unit into 1st and 2nd stage cooling and checked charge. had to add charge to 2nd stage. sight glass full. distributor tubes cold. both stages working normally. re-glued pvc trap and vacuumed drain pan. | Preventive Maintenance
188150 | pm unit for cooling season | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-04-21 | 2021-04-28 | removed air deflectors and thoroughly cleaned condenser coils. checked condenser fan operation. lubricated blower motor and bearings. checked belt tension. placed unit into 1st and 2nd stage cooling and checked charge. found off timer and contactor bad on 2nd stage. replaced. tested. sight glass full. distributor tubes cold. both stages working normally. re-glued pvc trap. vacuumed drain pan. | Preventive Maintenance
196554 | Replace air filters and belts for HVAC airside equipment | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-06-28 | 2021-06-30 | 1. Replaced all air filters to obtain a final air filtration efficiency of MERV 13. 2. Addressed air bypass around air filters. 3. Lubricate all damper shafts 4. Verify proper operation of outdoor air dampers. 5. Replace belts. 6. Lubricate fan bearings | Preventive Maintenance
198470 | check exhaust fan operation | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-07-15 | 2021-07-15 | checked exhaust fan operations. all fans working. | Preventive Maintenance
199897 | pm ductless units | Declined | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-07-29 |  |  | Preventive Maintenance
204616 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-09-01 04:48 | 2022-03-09 | Performed annual heating maintenance and checks. | Preventive Maintenance
204617 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-09-01 04:48 | 2022-03-09 | Performed annual heating maintenance and checks. Submitted a repair request to Rob with HCPSS. | Preventive Maintenance
204618 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-09-01 04:48 | 2022-03-09 | Performed annual heating maintenance and checks. | Preventive Maintenance
204619 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-09-01 04:48 | 2022-03-09 | Performed annual heating maintenance and checks. | Preventive Maintenance
204620 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-09-01 04:48 | 2022-03-09 | Performed annual heating maintenance and checks. | Preventive Maintenance
204621 | Monthly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-09-01 04:48 | 2022-03-09 | Performed annual heating maintenance and checks. | Preventive Maintenance
212771 | Yearly - CAN WASH-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-11-06 00:57 | 2021-11-16 | tested heater. working normally. | Preventive Maintenance
212838 | Yearly - MECH RM HTR-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-11-06 00:58 | 2021-11-16 | tested heater. working normally. | Preventive Maintenance

## 2021 NON PM HTG Work Orders
WOID | Description | Status | Craft | Location | Request Date | Actual Completion Date | Action Taken | Purpose
177638 | rtu sw and mp in fan alarm | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-01-14 | 2021-01-14 | 1/12/21: inspected rtu's and found running normally. no issue. inspected pressure switches for fan status. connections good. temps in area within county guidelines. | General Maintenance
178279 | rtu sw in alarm for fan status | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-01-25 | 2021-01-25 | 1/22/21: arrived and found unit running but status in alarm. delay in alarm to clear issue. unit running fine. got list of materials needed for compressor oil change. | General Maintenance
182561 | Temp. reading at 60 in cafeteria front office said its to cold | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-03-01 | 2021-03-02 | -Inspected office area temp was 71.0 made slight adjustment due to office staff being cold made adjustment and set temp one degree higher 3/2/21 8:30am -Inspected cafeteria, temp was reading 69.7 degrees normal temperature range.I spoke to The Assistant principal about the temp range and told her the temperature was in normal range and that if she would like to have it changed to put in a request/ticket 3/2/21 9:00am Met with contractors To get proper measurements of exhaust fan. contractors Said they will need a crane to get the old exhaust fan off roof, did not Give details on when they will return To finish job 10:15am 3/2/21 | General Maintenance
182762 | Cafeteria is extremely cold in the morning. Below 69 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-03-02 | 2021-03-02 | Te cafeteria will below temperature before it start in the morning. Had technician over today about cafeteria was cold from yesterday . He check temperature at 8:30am and it was 69.5 in the cafeteria. The county guidelines for heating are 68-70 in the space. | General Maintenance
183223 | locate for hood breaker | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-03-05 | 2021-03-05 | 3/5/21: went to kitchen to locate breaker. talked with kitchen staff. showed me panel behind prepared lunches. found breaker marked Hood Fan. Turned off and checked for power on roof. no power. | General Maintenance
183481 | meet contractor/crane for kitchen exhaust replacement | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-03-09 | 2021-03-10 | 3/8/21: met with contractor and showed them location of fan. | General Maintenance
183416 | Pick up old ex-fan and take to dump. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-03-09 | 2021-03-11 | Picked up ex-fan and took to dump. | General Maintenance
184210 | Temp. reading in cafe is 55 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-03-15 | 2021-03-17 | 3/15/21: checked temp in cafeteria and reading 68 degrees. reading 69 degrees in BAS. will return and install data logger to monitor. 3/17/21: installed data logger. | General Maintenance
184482 | pm heating pump | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-03-17 | 2021-03-17 | 3/17/21: added oil and coolant to work vehicle. Pm'd heating pump. checked amp draws. lubricated motor. | General Maintenance
184520 | set stats to Fan ON | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-03-17 | 2021-03-17 | 3/17/21: picked up pm parts from the shop. Arrived at school and set all portable stats to FAN ON per Larsen Angel. | General Maintenance
184941 | cafeteria cold | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-03-22 | 2021-03-22 | 3/19/21: inspected unit and found oa open 100%. oa damper regulator set screw loose letting damper open all the way up. reset back to 15% open minimum. locked down set screw. adjusted supply air temp up. cafeteria temp maintaining at 70 degrees. left data logger in cafeteria. | General Maintenance
192455 | Adjust rtu supply air temps | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-05-25 | 2021-05-27 | 5/25/21: went around building and adjusted supply air controls to supply 55 degree air to space. checked air compressor. working normally. day chief had issue with hissing from sw control box. just controller bleeding air. | General Maintenance
192457 | Teacher says room hot | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-05-25 | 2021-05-28 | 5/27/21: checked classroom and temp 71 degrees after adjusting rtu supply air temps. stat set for 71 degrees. working normally. | General Maintenance
194251 | office warm | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-06-08 | 2021-06-09 | 6/8/: when arrived I took a temp of main office and temp 72 degrees. rtu-o discharging 57 degree air. principal secretary said temp is good now. was warm and humid when they first got in. informed them to give system time manage space temp. | General Maintenance
195430 | Carpets are being cleaning on and 6/18 please run all ac units to help with the drying. 7AM-6PM | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-06-16 | 2021-06-21 | Scheduled | General Maintenance
196561 | Equipment reporting high Temps. Server Room | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-06-28 | 2021-07-09 | 6/30/21 work order put in without purpose and craft not allowing routing. Checked out, replaced batteries in remote. Started unit and it was running fine at this time. Batteries came from office in school. 2 AAA | General Maintenance
200992 | Check office unit after power failure | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-06 | 2021-08-06 | Checked units after power failure. Office unit came back on by the time I got there. Checked filter spacers and dampers. School only had 4 of 8 units running made list of problems and sent Larson. RTSE need damp motor replaced it leaks air. Also a few dampers were open some and should have been closed looking at the metasys. Dampers at school need to be checked on a normal running day. | General Maintenance
201476 | Need air conditioning to be on for the weekend 6am to 6pm through out the building for floor work to be done. Next week left on until 9pm | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-11 | 2021-08-12 | Schedules added | General Maintenance
201701 | Ceiling Tile Replaced:Principal Office,Work Room,Boys bathroom near 112,Server Room,Classrooms:132,131,130,116,103 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-13 | 2021-10-11 |  | General Maintenance
201955 | No air in cafeteria | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-16 | 2021-08-17 | 8/16/21: found space temp 76 degrees. reviever controller for supply air out of calibration. calibrated. cooling staged on and dropped temp to 73 degrees. cooling cycling between 72-75 degrees. | General Maintenance
202037 | Need air throughout the building until 9pm doing floors the rest of the week | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-16 | 2021-08-17 | Schedules added | General Maintenance
202431 | The building is hot, HEAT IS BLOWING | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-19 | 2021-08-20 | 8/19/21: found all areas in full heat. air compressor tripped out from power outage and has not pressure. started up air compressor and built pressure back up in building. all heat shut off. occupied building rtu's and cooling came on. monitored space temps until they got down with in county temp guidelines. | General Maintenance
202532 | No air in portable 257 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-19 | 2021-08-25 | 8/20/21:found stat setting to 85 degrees. running on a schedule. found stat never set up from installation. set up stat but keeps trying to run on a schedule. will get new stat and match to other portables. 8/24/21: installed new stats and tested on 2 new portables. | General Maintenance
202697 | Air is not on in the building | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-20 | 2021-08-20 | 8/20/21: hvac units are running on regular school schedule and do not start up until 740am | General Maintenance
202944 | adjust portable stats | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-23 | 2021-08-23 | changed all portable stats to FAN AUTO catch up on oa damper paperwork | General Maintenance
203370 | Panasonic Inverter not cooling in the gym office | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-25 | 2021-08-26 | 8/25/21: inspected unit and found batteries dead in remote. installed new batteries and unit started up and discharging 54 degree air. also found bad condensate pump. went to supply house and got new pump. will return to replace. 8/26/21: returned and replaced pump. had to drill new holes in block wall as new pump wider than old pump. poured water in pump and tested. working normally. started ac back up. | General Maintenance
203478 | recheck damper operation | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-25 | 2021-08-25 | 8/24/21: rechecked damper operation. found programming issue with outside air dampers closing when temp is over 80 degrees. Frank L. fixed issue | General Maintenance
203706 | rtu-o in alarm supply fan not running | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-26 | 2021-09-02 | 8/26/21: inspected unit and found no supply fan operation. no 24v control volts. missing a leg of power to unit. fuse blown in disconnect. retrieved new fuse. when new fuse installed and unit started control board blew. short somewhere. will get new board and return to find short. 8/27/21: installed new board and transformer. started up unit. working normally. | General Maintenance
203716 | Air is not working in the office | Duplicate Request | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-26 |  | reference Work Order: 203706 | General Maintenance
204147 | Air is not on in room 116 very hot. | Duplicate Request | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-30 |  | reference Work Order: 204241 | General Maintenance
204241 | No air in back pod (112-116) | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-31 | 2021-09-03 |  | General Maintenance
204254 | no air in caferteria | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-08-31 | 2021-09-03 | Inspected area temperature was reading 73 degrees | General Maintenance
205762 | heat always running | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-09-09 | 2021-09-09 | 9/3/21: inspected and found that as soon as unit is powered heat comes on in gym rtu. inspected controls and found no pressure on receiver controller. inspected lines and nite PE switch closed. no leak at pe switch but found loose air line on night stat. repaired air line. heat working normally now. gym rtu running with no heat. | General Maintenance
205984 | No air in room 113 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-09-10 | 2021-09-23 | checked space temp and temp 74.8 degrees. diffusers discharging 62 degree air. RTU-NE just was only running for 15 min and working normally. felt airflow from all diffusers. | General Maintenance
206038 | No air in portable 234 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-09-10 | 2021-09-20 | 9/13/21: checked unit and found low battery on stat. replaced batteries. unit not coming on when stat calling. inspected bard unit and smelled a burnt electrical smell. no 24v at terminal block. transformer bad. went to shop/supply house to pick up. returned and installed new transformer. unit came on and cooling normally. | General Maintenance
206261 | repair oa damper | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-09-13 | 2021-09-13 | 9/13/21: repaired oa damper actuator and arm. tested RTU-O in economizer and set min OA set point. both working normally. checked by both techs. | General Maintenance
206263 | repair OA damper and re-check operation | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-09-13 | 2021-09-13 | 9/13/21: oa dampers not opening. issue with signal from controller. had frank L. also inspect. signal now working but ep2 bad. repaired. damper working now. verified by Josh and Frank L. | General Maintenance
206143 | Need air conditioning on this week until 8pm for Back to School Night on Monday (tonight), Tuesday (tomorrow) and Wednesday | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-09-13 | 2021-09-13 | Scheduled | General Maintenance
207433 | Panasonic Inverter leaking water | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-09-23 | 2021-09-24 | was told water coming from gym office ductless unit. teacher said water coming from where refrigerant lines are run. said it was dripping before the rain. cool outside and teacher had gym ac set low. could have frozen up lines. set to 71 degrees. running normally. | General Maintenance
209297 | Need air conditioner on tomorrow (10\9) for work being done in the building | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-10-08 | 2021-10-08 | Scheduled. In the future please include areas and times needed. | General Maintenance
209821 | Need to repair or replace all condensate line supports. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-10-14 | 2021-10-20 | checked roof and all drains terminate at roof drains | General Maintenance
210154 | 55 degrees in portable 113 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-10-18 | 2021-10-20 | checked portable and found 59 degrees. calling for heat but not running. fan and compressor wont run. unit had burnt smell. found transformer blown. went to supply house to get parts. changed 2 contactors, capacitor and transformer. unit working now. 10/25/21: rechecked space to make sure still working normally. space temp within county guidelines. | General Maintenance
212368 | Temp. reading at 54 degrees | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-11-03 | 2021-11-04 | 11/3/21: checked and found gas heat not running on RTU MC. found loose wire connector on heat control board. reconnected and gas heat started up. working normally now. | General Maintenance
213899 | 59 degrees in gym | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-11-15 | 2021-11-17 | 11/16/21: found gas heat not running. volume controller out of calibration. re-calibrated and heat running. will monitor and re-adjust if necessary. 11/17/21: checked and space heated to 72 degrees. | General Maintenance
215783 | Gym unit not running | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-12-01 | 2021-12-01 | Receiver controller needed to be adjusted set to 8 psi | General Maintenance
217715 | Portable 4 temp. reading 37 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-12-20 | 2022-02-15 | 11/20/21- Traveled to site and checked in with the front office. Discovered that portable 4 is actually P204. Room temperature was 42F. No airflow was coming from the vents. Found at the unit that the blower motor was humming loudly as well as hot to the touch. Amp draw was well over the rated 2.5A at 4.6A. The capacitor is still functional, reading 4.9mfd out of 5. Blower motor needs replaced. Received permission to proceed with repairs. United Refrigeration asked me to bring in the old motor to aid in sourcing the replacement. Cut out motor, took it to United, and ordered a replacement. Will need to return to complete repair after parts arrive.12-22-21 removed bad motor and installed new replacement. Tested for function everything operates perfectly. Job is complete. | General Maintenance
217824 | Space heater, we were given 2 for portable 204 one is not working | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-12-21 | 2021-12-22 | 12/21/21: found that having 2 heaters on same circuit tripped breaker. lowered heat setting to see if breaker doesnt trip. | General Maintenance
217960 | install heaters | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2021-12-22 | 2021-12-22 | 12/21/21: picked up heaters from shop and installed in classroom. | General Maintenance

## 2020 PM HTG Work Orders
WOID | Description | Status | Craft | Location | Area Desc | Request Date | Actual Completion Date | Action Taken | Purpose
146945 | HOT WATER HEATING BOILER # 1 PREVENTIVE MAINTENANCE AND SAFETY DEVICE EXERCISES. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | Boiler Room | 2020-01-24 | 2020-01-27 | 01/24/2020. I checked the hot heating water building pump operation, checked the hot water heating boiler circulator pump operation, checked the hot water heating boiler and associated equipment for signs of water leakage, none found at this time. I checked the hot water heating boiler current operating pressure @ 30 P.S.I., checked the combustion air damper mechanism operation, checked the primary burner control sequence of operation, checked the modulation linkage operation, checked the main gas valve closure response time, checked the combustion air fan proving switch normally open contacts resting position, checked the primary burner control response to terminate or lockout a active operation cycle until a manual reset takes place when combustion air fan proving switch normally open contacts remain open during a pre purge period of a cycle creating a absence of a proven interlock, exercised a simulated pilot flame absence during a trial for ignition period of cycle and the primary burner control response to terminate or lockout the operation cycle until a manual reset takes place due to the absence of a proven interlock, exercised a exceeded high water temperature limit set point and the primary burner control response to terminate or prevent a active operation cycle when open contacts are present at the high water temperature limit safety device, exercise the primary burner control response to terminate or prevent a active operating cycle during a simulated low water condition and resulting open contacts at the mechanical low water cutoff safety device, exercised the primary burner control response to terminate or prevent a active operating cycle with open contacts at a functional low gas pressure supply safety device during a simulated low natural gas supply pressure condition, checked the flame signal strength, exercised the hot water heating boiler alarm text alert messaging service response, flushed the hot water heating boiler. CONTINUED IN JOURNAL NOTES. | Preventive Maintenance
147726 | Yearly - BWES-AIR COMPRESSOR-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-02-01 04:33 | 2020-02-06 | 2/5/20: picked up parts for PM 2/6/20: performed pm on both compressors. changed oil, belts and air filters. checked all connections and all working properly. ordering new filters for water and oil. | Preventive Maintenance
148039 | HOT WATER HEATING BOILER # 1, PREVENTIVE MAINTENANCE AND SAFETY DEVICE EXERCISES. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | Boiler Room | 2020-02-03 | 2020-02-03 12:39 | 02/03/2020. I checked the hot heating water building pump operation, checked the hot water heating boiler circulator pump operation, checked the hot water heating boiler and associated equipment for signs of water leakage, none found at this time. I checked the hot water heating boiler current operating pressure @ 25 P.S.I., checked the combustion air damper mechanism operation, checked the primary burner control sequence of operation, checked the modulation linkage operation, checked the main gas valve closure response time, checked the primary burner control response to terminate or lockout a active operation cycle until a manual reset takes place when combustion air fan proving switch normally open contacts remain open during a pre purge period of a cycle creating a absence of a proven interlock, exercised a simulated pilot flame absence during a trial for ignition period of cycle and the primary burner control response to terminate or lockout the operation cycle until a manual reset takes place due to the absence of a proven interlock, exercised a exceeded high water temperature limit set point and the primary burner control response to terminate or prevent a active operation cycle when open contacts are present at the high water temperature limit safety device, exercise the primary burner control response to terminate or prevent a active operating cycle during a simulated low water condition and resulting open contacts at the mechanical low water cutoff safety device, exercised the primary burner control response to terminate or prevent a active operating cycle with open contacts at a functional low gas pressure supply safety device during a simulated low natural gas supply pressure condition, checked the flame signal strength, exercised the hot water heating boiler alarm text alert messaging service response, flushed the hot water heating boiler, flushed the safety relief valve. CONTINUED IN JOURNAL NOTES. | Preventive Maintenance
150626 | HOT WATER HEATING BOILER # 1, PREVENTIVE MAINTENANCE AND SAFETY DEVICE EXERCISES. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | Boiler Room | 2020-02-24 | 2020-02-24 12:43 | 02/24/2020. I checked the hot heating water building pump operation, checked the hot water heating boiler circulater pump operation, checked the hot water heating boiler and associated equipment for signs of water leakage, none found at this time. I checked the hot water heating boiler current operating pressure @ 25 P.S.I., checked the combustion air damper mechanism operation, checked the primary burner control sequence of operation, checked the modulation linkage operation, checked the main gas valve closure response time, checked the combustion air fan proving switch normally open contacts resting position, checked the primary burner control response to terminate or lockout a active operation cycle until a manual reset takes place when combustion air fan proving switch normally open contacts remain open during a pre purge period of a cycle creating a absence of a proven interlock, exercised a simulated pilot flame absence during a trial for ignition period of cycle and the primary burner control response to terminate or lockout the operation cycle until a manual reset takes place due to the absence of a proven interlock, exercised a exceeded high water temperature limit set point and the primary burner control response to terminate or prevent a active operation cycle when open contacts are present at the high water temperature limit safety device, exercise the primary burner control response to terminate or prevent a active operating cycle during a simulated low water condition and resulting open contacts at the mechanical low water cutoff safety device, exercised the primary burner control response to terminate or prevent a active operating cycle with open contacts at a functional low gas pressure supply safety device during a simulated low natural gas supply pressure condition, checked the flame signal strength, exercised the hot water heating boiler alarm text alert messaging service response, flushed the hot water heating boiler. CONTINUED IN JOURNAL NOTES. | Preventive Maintenance
151661 | Yearly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Declined | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-03-01 06:12 |  | COVID 19- Change is being made by HCPSS Tech when school filters are replaced due to change to MERV13 7/1/2020. Will resume on 9/1/20 with Emjay | Preventive Maintenance
151662 | Yearly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Declined | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-03-01 06:12 |  | COVID 19- Change is being made by HCPSS Tech when school filters are replaced due to change to MERV13 7/1/2020. Will resume on 9/1/20 with Emjay | Preventive Maintenance
151663 | Yearly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Declined | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-03-01 06:12 |  | COVID 19- Change is being made by HCPSS Tech when school filters are replaced due to change to MERV13 7/1/2020. Will resume on 9/1/20 with Emjay | Preventive Maintenance
151664 | Yearly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Declined | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-03-01 06:12 |  | COVID 19- Change is being made by HCPSS Tech when school filters are replaced due to change to MERV13 7/1/2020. Will resume on 9/1/20 with Emjay | Preventive Maintenance
152095 | HOT WATER HEATING BOILER # 1, PREVENTIVE MAINTENANCE AND SAFETY DEVICE EXERCISES. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | Boiler Room | 2020-03-03 | 2020-03-03 | 03/03/2020. I checked the hot heating water building pump operation, checked the hot water heating boiler circulater pump operation, checked the hot water heating boiler and associated equipment for signs of water leakage, none found at this time. I checked the hot water heating boiler current operating pressure @ 30 P.S.I., checked the combustion air damper mechanism operation, checked the primary burner control sequence of operation, checked the modulation linkage operation, checked the main gas valve closure response time, checked the combustion air fan proving switch normally open contacts resting position, checked the primary burner control response to terminate or lockout a active operation cycle until a manual reset takes place when combustion air fan proving switch normally open contacts remain open during a pre purge period of a cycle creating a absence of a proven interlock, exercised a simulated pilot flame absence during a trial for ignition period of cycle and the primary burner control response to terminate or lockout the operation cycle until a manual reset takes place due to the absence of a proven interlock, exercised a exceeded high water temperature limit set point and the primary burner control response to terminate or prevent a active operation cycle when open contacts are present at the high water temperature limit safety device, exercise the primary burner control response to terminate or prevent a active operating cycle during a simulated low water condition and resulting open contacts at the mechanical low water cutoff safety device, exercised the primary burner control response to terminate or prevent a active operating cycle with open contacts at a functional low gas pressure supply safety device during a simulated low natural gas supply pressure condition, checked the flame signal strength, exercised the hot water heating boiler alarm text alert messaging service response. CONTINUED IN JOURNAL NOTES. | Preventive Maintenance
152996 | greasing pump motor's | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | Boiler Room | 2020-03-09 | 2020-03-10 08:42 | greased pump bearings for pump #1(3-9-2020) | Preventive Maintenance
153800 | stats need lock box/cover | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | Portables | 2020-03-13 | 2020-03-18 | put new lockbox/cover's on all stats in portable's | Preventive Maintenance
155263 | Yearly - DX OFFICE UNIT-BRYANT WOODS-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-05-01 03:39 | 2020-05-15 | 5/14/20: inspected unit and greased bearings. checked operation of all motors and compressors. All working normally. compressors have refrigerant charge. Too cool outside to accurately check charge. Tightened all connections on starters. Belts and filters changed 10/19. | Preventive Maintenance
157344 | HOT HEATING WATER EQUIPMENT CHECK AFTER EXTENDED CLOSURE DUE TO COVID-19. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | Boiler Room | 2020-06-05 | 2020-06-08 07:48 | 06/05/2020. I checked the hot heating water plant equipment for signs of water leakage none found at this time, checked the current hot water heating boiler operating pressure @ 30 P.S.I., checked the primary burner control sequence of operation, checked the hot heating water building pump operation, checked the hot water heating boiler circulator pump operation, checked the combustion air damper operation, checked the BAS. All is running as designed currently. | Preventive Maintenance
157706 | Yearly - Boiler PM-Bryant Woods ES-Yearly - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-06-10 01:03 | 2020-07-08 | I cleaned the boiler room , sweeping , vacuuming , washing equipment , piping , and other flat dirt covered surfaces . I checked the gas vent terminations , checked the combustion air damper operation , flushed the low water cut off float chamber , flushed the safety relief valve , checked the burner sequence of operation , checked the ignition transformer out put voltage , checked the gas pressure @ 2.60 I.W.C. , recorded combustion analysis values , exercised the burner operating control , exercised the burner alarm text alert messaging service , exercised the low water cut off , exercised the burner control reaction to a open contact at the combustion air fan proving switch . | Preventive Maintenance
159612 | Yearly - Filter Change-Bryant Woods ES-Yearly - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-07-01 03:56 | 2020-08-20 | replaced all filters | Preventive Maintenance
159744 | Yearly - Belt Change-Bryant Woods ES-Yearly - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-07-01 03:58 | 2020-08-19 | REPLACED BELTS FOR RTUS | Preventive Maintenance
165888 | Yearly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-09-03 01:11 | 2020-10-19 | Completed annual heating maintenance and checks. | Preventive Maintenance
165889 | Yearly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-09-03 01:11 | 2020-10-19 | Completed annual heating maintenance and checks | Preventive Maintenance
165890 | Yearly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-09-03 01:11 | 2020-10-19 | Completed annual heating maintenance and checks. | Preventive Maintenance
165891 | Yearly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-09-03 01:11 | 2020-10-19 | Completed annual heating maintenance and checks. | Preventive Maintenance
165892 | Yearly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-09-03 01:11 | 2020-12-02 | Completed annual heating maintenance and checks. | Preventive Maintenance
165893 | Yearly - Portable PM-Bryant Woods-Semi Annual - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-09-03 01:11 | 2020-10-19 | Completed annual heating maintenance and checks. Installed new auto changeover t stat and lockbox box supplied by hccps. C. | Preventive Maintenance
172843 | Yearly - CAN WASH-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-11-06 00:47 | 2020-11-17 | 11/10/20: tested heater. working normally. | Preventive Maintenance
172911 | Yearly - MECH RM HTR-BWES-YEARLY - Refer to PM schedule details. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES |  | 2020-11-06 00:47 | 2020-11-17 | 11/10/20: tested heater in boiler room and water heater room. working normally. | Preventive Maintenance

## 2020 NON PM HTG Work Orders
WOID | Description | Status | Craft | Location | Request Date | Actual Completion Date | Action Taken | Purpose
144419 | CHECK THE OPERATING STATUS OF THE HOT WATER HEATING PLANT EQUIPMENT, DUE TO RECENT LOW WATER TEMPERATURE ALARM, AS INSTRUCTED. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-01-02 | 2020-01-03 06:22 | 01/02/2019 I checked the hot water heating plant equipment for signs of water leakage, none found at this time. I checked the current hot water heating boiler operating pressure @ 28 P.S.I., checked the hot water heating boiler primary control sequence of operation, checked the combustion damper operation, checked the hot heating water building pump operation, checked the hot water boiler circulator pump operation,checked the natural gas valve closure response time, checked, checked the for and aft observation port assemblies, checked the hot heating water loop temperature via the BAS, checked the hot heating water mixing valve position via the BAS computer. No problems detected or action taken at this time. | General Maintenance
145093 | Cafeteria cold mini temp. 58 | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-01-08 | 2020-01-09 | 1/8/19: inspected on BAS and found temp 61 degrees in space. RTU MP running but not heating. Found PE switch for heat. heating board not working. reset main power to unit. board back online and gas heat started up. space heated to 72 degrees. generator test probably tripped out board. | General Maintenance
148962 | Vent cover fell from the ceiling tile in staff bathroom next to the art room at the end of the hall | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-02-11 | 2020-02-18 | 2/13/20: inspected bathroom and found broken vent. will return with new vent. 2/18/20: returned with new vent. drilled new screw holes in duct. secured vent to ceiling. | General Maintenance
150880 | Always keep as an IEQ craft 1. RTU-MC and RTU- KA- It appears the outside air dampers are completely closed. 2. Return fans of all RTUs not running and based on the conditions it appears they may not have ran in a long time. 3. RTU-? (only one unit) condensate drain piping not properly terminated. 4. No tag numbers on any EFs. 5. EF next to RTU-O is rattling. 6. EF between RTU-0 and café roof not running. 7. Appears a Trane RTU is abandoned on the high café roof. 8. Portable 113 and 118- stat front cover missing. Portable 234 no stat front cover or base. Return air grille very dirty. 8. RTU-NW old abandoned motor sitting outside next to the unit. 9. Gym diffusers cones missing. 10. Old motor on the roof. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-02-25 | 2020-06-05 | 6/5/20: 1) Checked all OA dampers. Dampers are cracked. not in economizer mode. 2) power exhaust fans only run when oa dampers open in economizer mode. Tested all power exhaust motors and all motors ran. 3) When condensate drains from RTU NE the water goes into roof drain 4) No exhaust fans were tagged when they were installed. 5) Tightened lid to exhaust fan. no more rattling. 6) Exhaust fan running. 7) Unit is no longer in use, Installed stat covers on stats 8) Removed motor 9) will look into replacing diffusers. 10) removed motor | General Maintenance
152090 | HOT WATER HEATING BOILER PUMP # 2 GENERATES A STATUS ALARM TEXT MESSAGE AFTER HOURS ON 03/02/2020 @ 6:15 P.M. # 1(410)200-832. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-03-03 | 2020-03-03 | 03/03/2020. I checked the circulator pump operation, checked the coupling integrity, determined what device was responsible for energizing pump on command, determine what method is utilized to determine pump operation status. The status of the pump is determined by a flow switch located in the heating water recirc piping. I verified that the pump is turning on and off when the building automation system issues the commands but it seems that the status proving flow switch is not always breaking consistently to indicate to the building automation system that the pump is off thus generating nuisance text alert messaging responses when the there has been a command off but the closed contacts falsely indicate otherwise. I manually exercised the flow switch mechanism and lubricated its external moving parts. It seems to operating as designed at this time. I have recorded the model # and will purchase and install a new replacement if this problem persists. I fueled the HCPSS service van at the recreation and parks headquarters fuel depot. I returned to Mendenhall to drop off invoices, overtime sheet and procure parts used recently from my truck stock. | General Maintenance
154141 | Friday 3/20/2020 - Cleaning / disinfecting hard surfaces due to Coronavirus concerns. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-03-20 | 2020-06-01 | Friday 3/20/2020 - As instructed, cleaning / disinfecting hard surfaces throughout building due the Coronavirus concerns. | COVID-19
155823 | check out rtu's and exhaust fans | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-05-13 | 2020-05-15 | checked compressors and fans for all rtu units. all run normally. All units in unoccupied mode. found heating plant not running when nite stat calling for heating. talked with frank L and he reprogrammed heating plant. found exhaust fan 3,2,8 running. exhaust fan 2 is gym fan that was left in hand by the gym teacher from starter in gym storage room. fan 8 is bathroom exhaust that is connected directly to power and emailed John D. about installing timer switch in bathroom. fan 3 was left on by art teacher. | General Maintenance
155933 | exhaust fan not working | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-05-15 | 2020-06-05 | checked exhaust fan in boiler room, fan was not working I then checked the capacitor uF capacitor is working normal, found that fan motor is no good 5-14-20, called Lange Electric for new fan motor and blade not in stock at the moment waiting for order to replace motor 5-15-20 6-2-20 picked up new fan motor Begin installing JR2 6/3/20: finished installing motor. Found relay locking out motor. Motor has wall stat controlling it. Frank L removed relay command. Exhaust fan working normally. | General Maintenance
155928 | Both circuits low on charge | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-05-15 | 2020-06-05 | 5/14/20: found noisy compressors when doing rtu inspections. found both circuits low on charge. brought tools to inspect and repair on roof but got called away for emergency call. 6/4/20: found leak at bypass valve. repaired leak. pressure tested to 200 psi. held pressure for 45 min. checked with soap bubbles. evacuated unit to below 500 micorons and held vacuum. charged circuits. cooling system running. 55 degree discharge air. sight glass full. | General Maintenance
157055 | meet with contractor who is repairing walk in box | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-06-03 | 2020-06-03 | 6/1/20: met with contractor who is working on walk in box in kitchen. Also picked up strainer basket from Grainger for WLHS | General Maintenance
157135 | Had to let Maryland Mechanical into the Kitchen to work on the walk in Freezer. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-06-03 | 2020-06-03 | Was able to let Maryland Mechanical into the Kitchen and the roof to troubleshoot the walk in freezer. | General Maintenance
158292 | Please turn on the air conditioning in K, 1st grade, 2nd grade, and 3rd grade Thursday 6/18 from 7am-2pm. Thank you. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-06-16 | 2020-06-17 09:08 | Scheduled. | Equipment Scheduling
158293 | please turn the air conditioning on in the front office, 4th grade, 5th grade, and the media center at bryant woods es on Friday 6/19 from 7am-2pm. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-06-16 | 2020-06-17 09:12 | Scheduled | Equipment Scheduling
160333 | THE HOT WATER HEATING BOILER VACUUM BREAKER IS LEAKING. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-07-07 | 2020-07-07 | 07/07/2020. I isolated the hot water heating boiler, drained the boiler below the low water cut off to remove the existing part. I replaced the existing, leaking part with a new part, refilled boiler and monitored for water leaks during operation. I checked the combustion damper operation, checked the water heating boiler sequence of operation, checked the hot heating water building pump operation, checked the hot water heating boiler injection pump operation, checked the primary burner control sequence of operation, checked the hot water heating boiler operating pressure. | General Maintenance
160520 | Please turn on air conditioning in Zone 3, Zone 4, and Zone 6 the week of July 13th-17th from 7am-6PM. Night supervisor works until 11PM. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-07-08 | 2020-07-10 | Scheduled | Equipment Scheduling
160451 | cut off portables | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-07-08 | 2020-07-08 | portables are still on due to custodial staff still waxing floors | General Maintenance
161886 | Request to have air turn on for 7\22 -7\24 and 7\27 -7\31 from 7am - 6pm working through out the building | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-07-22 | 2020-07-23 | Scheduled | Equipment Scheduling
162392 | Multiple units are tripped. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-07-24 | 2020-09-17 | 7/24-Found RTU's RTUMP/RTUSW both tripped on high pressure. Reset them and they came on and cooled. RTUO (Office unit) was not running at all. Found a low voltage issue leading to the blow relay not engaging. Traced the loss of voltage throughout the RTU and down to the control cabinet in the custodial office. Traced the issue back up to the 2nd stage cooling in the unit and found a bad compressor contactor. Notified Rob G and he is ordering a new one. Will install when the part comes in. At the moment, the unit is running in 1st stage cooling only. 9/17-Picked up a new contactor/auxiliary contactor from Aireco. Installed them both and ensured that the unit would run. | General Maintenance
163234 | Leak coming through broken exhaust hood in kitchen. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-08-04 | 2020-08-04 | 8/4-Met with roofers on site. Exhaust fan on the roof is missing its cover. It had a temporary tarp in place until repairs could be made. Borrowed a new tarp from one of the roofers and secured it over top of the exhaust fan. Leak should hold until repairs can be made. | General Maintenance
163199 | Roof leaking in the middle of gym ceiling above exhaust duct work | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-08-04 | 2020-08-04 | This has been an ongoing leak for many years itÃƒÆ’Ã†â€™Ãƒâ€šÃ‚Â¢ÃƒÆ’Ã‚Â¢ÃƒÂ¢Ã¢â€šÂ¬Ã…Â¡Ãƒâ€šÃ‚Â¬ÃƒÆ’Ã‚Â¢ÃƒÂ¢Ã¢â€šÂ¬Ã…Â¾Ãƒâ€šÃ‚Â¢s an HVAC problem. 9/24/20: inspected and found catch can under ceiling where gas line and electric go up to gym rtu. Will return to inspect unit. 9/29/20: inspected unit and found that water may be leaking into unit due to bad door gasket. will try and order new gasket from havtech. 10/7/20: picked up gasket from havtech 10/9/20: installed new gasket material around rtu gym doors. 10/13/20: inspected after weekend weather and found no water in unit. will monitor | General Maintenance
163217 | HOT WATER HEATING BOILER #1 TO BE RETURNED TO NORMAL SERVICE AFTER REPAIR TO BACK FLOW PREVENTER NOW COMPLETED. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-08-04 | 2020-08-04 | 08/04/2020. I enable the hot water heating boiler, observed operation, checked the primary burner control sequence of operation, checked the hot water heating plant equipment for signs of water leakage, none found at this time, checked the combustion damper operation, checked the hot water heating boiler circulator pump operation, checked the hot heater water building pump operation, checked the current hot water heating boiler operating pressure @ 30P.S.I. | General Maintenance
164134 | Request to have air turned on for the week of 8/17 - 8\21 7am - 6 pm working throughout the building. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-08-13 | 2020-08-13 | Scheduled | Equipment Scheduling
167376 | Room 113 work was done on a unit in the ceiling, tile and light was moved. Where are we with this work for completion? | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-09-15 | 2020-09-23 | Josh will complete after doing all the check out of the exhaust fans in all his building. | General Maintenance
168747 | EF-2 NOT WORKING | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-09-24 | 2020-10-01 | 9/30/20: investigated fan. no power to fan on roof. looked at prints and found breaker. breaker had been removed and used for gym office ac. gym storage vent removed. ef-2 is no longer in use. informed Frank L. | General Maintenance
168748 | EF-5 NOT WORKING | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-09-24 | 2020-10-01 | 9/24/20: inspected EF-5 in boiler room per chart. found override released in bas for fan. put override back on in BAS. Frank L. aware override for relay needs to remain on. Fan now working properly off of wall thermostat. | General Maintenance
168749 | EF-8 NOT WORKING | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-09-24 | 2020-10-01 | 9/24/20: inspected prints to see how fans are started and connected to system. 9/30/20: followed wiring and found ex 8 for bathroom tied into wall outlet in office. Informed Frank L. May need to have electrician install timer switch or tie into BAS system. | General Maintenance
169869 | replace air dryer and filter system | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-10-08 | 2020-10-09 | 10/6/20: picked up parts to complete job 10/8/20: removed old air dryer and installed new one. connected all lines and tested. re-pressurized tank and turned systems back on. working normally | General Maintenance
169872 | Meet with Frank L. to check/set OA damper minimums | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-10-08 | 2020-10-08 | 10/7/20: set all oa dampers to proper minimum using calculation provided by supervisor. | General Maintenance
170010 | fan status in alarm | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-10-09 | 2020-10-14 | 10/9/20: inspected unit. found main power but no low voltage power. fuse blown. went to shop for new fuses. installed. unit running normally. 11/9/20: found rtu se in alarm. no 24v power. found burnt fuse. fuse block may be bad. ordered from havtech. will return to replace parts when they arrive. 11/17/20: picked up parts from supply house that arrived. returned and installed new terminal block and fuses. put spare parts in grey cabinet. powered up unit and tested. monitored amp draw and thermal reading on fuses. unit ran all day without blowing fuses and went to unoccupied at scheduled time. | General Maintenance
170898 | HOT WATER HEATING BOILER # 1 PREVENTIVE MAINTENANCE AND SAFETY DEVICE EXERCISES. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-10-22 | 2020-10-22 | 10/22/2020. I checked the hot heating water building pump operation, checked the hot water heating boiler circulater pump operation, checked the hot water heating boiler and associated equipment for signs of water leakage, none found at this time. I checked the hot water heating boiler current operating pressure @ 30 P.S.I., checked the combustion air damper mechanism operation, checked the primary burner control sequence of operation, checked the modulation linkage operation, checked the main gas valve closure response time, checked the combustion air fan proving switch normally open contacts resting position, checked the primary burner control response to terminate or lockout a active operation cycle until a manual reset takes place when combustion air fan proving switch normally open contacts remain open during a pre purge period of a cycle creating a absence of a proven interlock, exercised a simulated pilot flame absence during a trial for ignition period of cycle and the primary burner control response to terminate or lockout the operation cycle until a manual reset takes place due to the absence of a proven interlock, exercised a exceeded high water temperature limit set point and the primary burner control response to terminate or prevent a active operation cycle when open contacts are present at the high water temperature limit safety device, exercise the primary burner control response to terminate or prevent a active operating cycle during a simulated low water condition and resulting open contacts at the mechanical low water cutoff safety device, exercised the primary burner control response to terminate or prevent a active operating cycle with open contacts at a functional low gas pressure supply safety device during a simulated low natural gas supply pressure condition. CONTINUED IN JOURNAL NOTES. | Boiler
174714 | drop off parts | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-12-01 | 2020-12-01 | 11/23/20: drop off extra parts to boiler room | General Maintenance
174720 | RTSE 1st Grade | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-12-01 | 2020-12-03 | 12/2/20: checked unit and found no 24v power. found transformers tripped. checked components for shorts. none found. reset and unit came on and running normally. will monitor. May be a power issue. 12/10/20: investigated on BAS and found that occasionally units trips out 20 sec after going into occupied. checked all connections again. took voltage readings. manually put into heat and gas heat started. could not duplicate result. adjusted start time from 7am to 7:05am. will monitor. | General Maintenance
175004 | HOT WATER HEARING BOILER # 1 PREVENTIVE MAINTENANCE AND SAFETY DEVICE EXERCISES. | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-12-04 | 2020-12-04 | 12/04/2020. I checked the hot heating water building pump operation, checked the hot water heating boiler circulator pump operation, checked the hot water heating boiler and associated equipment for signs of water leakage, none found at this time. I checked the hot water heating boiler current operating pressure @ 30 P.S.I., checked the combustion air damper mechanism operation, checked the primary burner control sequence of operation, checked the modulation linkage operation, checked the main gas valve closure response time, checked the combustion air fan proving switch normally open contacts resting position, checked the primary burner control response to terminate or lockout a active operation cycle until a manual reset takes place when combustion air fan proving switch normally open contacts remain open during a pre purge period of a cycle creating a absence of a proven interlock, exercised a simulated pilot flame absence during a trial for ignition period of cycle and the primary burner control response to terminate or lockout the operation cycle until a manual reset takes place due to the absence of a proven interlock, exercised a exceeded high water temperature limit set point and the primary burner control response to terminate or prevent a active operation cycle when open contacts are present at the high water temperature limit safety device, exercise the primary burner control response to terminate or prevent a active operating cycle during a simulated low water condition and resulting open contacts at the mechanical low water cutoff safety device, exercised the primary burner control response to terminate or prevent a active operating cycle with open contacts at a functional low gas pressure supply safety device during a simulated low natural gas supply pressure condition. CONTINUED IN JOURNAL NOTES. | Boiler
175517 | meet contractor | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-12-11 | 2020-12-11 | 12/10/20: met with Tim from MD Mechanical about kit exhaust replacement | General Maintenance
175932 | Friday 12/19/2020 - I received text message alarm stating Boiler is down on Flame Failure. (12:58am) | Closed Work Orders | Heating/Ventilation /Air Conditioning | Bryant Woods ES | 2020-12-19 | 2020-12-29 | Friday 12/19/2020 - Found Boiler down on Flame Failure. (Pilot) Reset boiler and failed again - Pulled pilot assembly and replaced igniter. Reset boiler and fired properly. Warmed up slowly. Satisfied on temp. before leaving. All OK at this time. Set alarm and secured building. | Call Out