## 2024 NON PM Roof Work Order
Status Category | Work Order # | Source Site | Work Category | Work requested | Assigned | Action Taken | Completed | Work Type
Archived | 0000017404 | Bryant Woods ES | Roof | water leaking from ceiling. room 128 | 04/04/2024 09:17:00 AM | 4/4/24-BT1- A little water was laying in the plastic of the light fixture and on a small corner of a ceiling tile. I went in the ceiling and detected no active leaks. I cut open the insulation on the nearest by piping and it was dry. It did rain heavily the past several days and this may be related to that. I replaced the ceiling tile and cleaned up. | 04/05/2024 02:06:00 AM | General Maintenance
Archived | 0000014999 | Bryant Woods ES | Roof | Patch a hole in the roof. | 03/13/2024 02:44:00 AM | Frank called about a hole in the roof. The contractor dropped something from the upper roof area. We patched. | 03/12/2024 03:34:00 AM | General Maintenance
Archived | 0000012562 | Bryant Woods ES | Roof | HVAC contractor accidentally put a hole in the roof and needs patched | 02/22/2024 07:02:00 AM | Talked to contractor, located the hole, and put down a PVC patch. | 02/22/2024 07:05:00 AM | General Maintenance
Archived | 0000008875 | Bryant Woods ES | Roof | water leaks in ceiling.... | 02/14/2024 08:12:00 AM | 3rd grade pod we patched 2 holes in the roof. Gym we patched several things that could have been leaking. | 02/12/2024 10:12:00 AM | General Maintenance
Assigned | 0000039782 | Bryant Woods ES | Roof | Leak upate on 9/30/24 Mr. Drew from HVAC went around school and checked all stained an water damage tiles he reported finding the Gym Office - 2 roofing leaks both inactive , Gym Storage -2 roofing leaks both inactive , Rm 105 -2 roofing leaks both inactive , Rm101 - 1 leak roofing screw hole near roof drain dripping directly on top of duct work .( Pic Attach) need looking into tiles keep getting wet when replace . Thanks | 10/01/2024 09:32:00 AM | Gym Office we need to prob the areas and patch what we find. Gym Storage found a hole in the flashing patched with caulk for now. Rm 105 found a few small open seams caulk them. Rm101 we found leak under the roof drain. We found a small hole we will need to return to patch |  | General Maintenance
Denied | 0000038725 | Bryant Woods ES | Roof | There is wet tiles cause by some tpye of leak in the CAFE ceiling also the celing in the cafe closet has dirt and debris falling out pics attch . | 09/25/2024 10:18:00 AM | Thursday 9/26/2024 (SK-1) - Roofing Dept. reported the condensate drain on the Cafeteria RTU is broken leaking water into the space below. Andrew Burns responded after the Roofing Dept. to repair the broken condensation drain line. Also, Frank Smith is scheduled to pick up the Genie lift first thing Friday morning and replace the damaged ceiling tiles in the Cafeteria. work preformed is on ticket 38975. |  | General Maintenance
Assigned | 0000038719 | Bryant Woods ES | Roof | There is wet tiles in ceililng do to leak somewhere pics attach/ also dirt debris falling down out the celing in cafe closet . | 09/25/2024 10:20:00 AM |  |  | General Maintenance
Archived | 0000011248 | Bryant Woods ES | Roof | walls are very wet. pictures are included(Associated work order from Erin 10135) | 02/06/2024 10:08:00 AM | 1/30/24 got in early before the kids came. Gym lead showed me where and what was happening. Looks like some leak up top. It’s coming from the exterior. Pooling in cinder. Leaking thru. Went on roof and noticed water pooling above spot. Metal caps look sound. There is a crack in brick that could b responsible. See pictures attached. Also popped up some corner guards in cafeteria 1/31/24 met with Bruce at Home Depot to pick up sika for the crack outside gymnasium. C picture attached. Started cleanout process of expansion joint using ladders and multi saw. Filled crack with backer rod. Gonna fill in w caulk in am. 2/1/24 caulk was not right . Got new. Van was at grounds this morning for oil change as well. 2/5/24 finished caulkin expansion joint. C pic. Needs to forward to roofing for further examination 2/12 We in roofing patched several areas near the scupper that are possible the source. |  | General Maintenance
Archived | 0000009982 | Bryant Woods ES | Roof | Leaks in multiple areas | 01/25/2024 02:38:00 AM | 1/25 AH-1 Looked at the active leaks with Andy. 1/26 AH-1 Found holes in all these areas and patched. Left the ceiling tiles stained because they were still dripping |  | General Maintenance

## 2024 PM Roof Work Order
Status Category | Work Order # | Source Site | Source Asset | Source Location | Work Category | Work requested | Assigned | Action Taken | Completed | Work Type | Created On
Archived | 0000030594 | Bryant Woods ES | BWES-ROOF-PVC |  | Roof | ROOF INSPECTION-BWES-SEMI ANNUAL | 07/23/2024 06:47:00 AM | These repairs were made per the roof inspection performed on 6/27/24 Level A: (1+6) Removed all deteriorated sealant on the coping cap and sealed with vulkem (2) Water disperses within 48 hours (3) Repaired pitch pocket with one flash and fabric (4) Removed any deteriorated caulk joints on vent pipes and sealed with vulkem (5) Removed any trash from roof Found a hole in the roof and patched. Level B: (2) Sealant has some age related deterioration but this does not leak. It is not safe to stand on this paneling Level C: Removed all debris and vegetation from roof Level D: (1) Water disperses within 48 hours (2) Removed deteriorated sealant on vent pipes and sealed with vulkem (3) Notified HVAC of broken condensation pipe Level E: (1) Water disperses within 48 hours (2) Removed trash from roof Level F: Water disperses within 48 hours | 07/24/2024 02:36:00 PM | Preventive Maintenance | 07/23/2024 06:47:30 AM
Assigned | 0000039658 | Bryant Woods ES | BWES-ROOF-PVC |  | Roof | ROOF INSPECTION-BWES-SEMI ANNUAL | 10/01/2024 06:20:00 AM |  |  | Preventive Maintenance | 10/01/2024 06:20:13 AM

## 2023 PM Roof Work Order
WOID | Description | Status | Craft | Location | Area Desc | Request Date | Actual Completion Date | Action Taken | Purpose
275175 | Monthly - ROOF INSPECTION-BWES-SEMI ANNUAL - Refer to PM schedule details. | Closed Work Orders | Roof | Bryant Woods ES |  | 2023-03-10 00:59 | 2023-04-11 07:45 | 3/10 Removed any debris, vegetation, and recess balls from the roof Cut out any bad caulk joints around the roof and resealed with vulkem Found a hole in the roof membrane and patched | Preventive Maintenance
286123 | PM the Roof | Closed Work Orders | Roof | Bryant Woods ES | Roof | 2023-06-07 | 2023-06-26 06:48 | Removed all debris and vegetation from the roof and from around the drains Removed all recess balls from the roof Checked roof for anything needing repair | Preventive Maintenance
298680 | Monthly - ROOF INSPECTION-BWES-SEMI ANNUAL - Refer to PM schedule details. | Pending | Roof | Bryant Woods ES |  | 2023-09-10 00:37 |  |  | Preventive Maintenance

## 2023 NON PM Roof Work Order
WOID | Description | Status | Craft | Location | Area Desc | Request Date | Actual Completion Date | Action Taken | Purpose
300486 | Please clean any debris in media center above ceiling. Likely from new office installations over summer | Closed Work Orders | Roof | Bryant Woods ES |  | 2023-09-22 | 2023-09-27 | We removed ceiling tiles and removed old dust that we found on top of the ceiling tiles. We also vac out the ceiling return grate that was full of dust. | General Maintenance
302921 | Check for stain tiles in the area of the media. | Closed Work Orders | Roof | Bryant Woods ES | Media Center | 2023-10-11 | 2023-10-13 | Checked the areas and found no new stained ceiling tiles. | General Maintenance
0000004498 | install new pipe for the mini-split | Archived | Roof | Bryant Woods ES | Roof | 2023-11-27 | 2023-11-27 | We met Tecta to install the new pipe. We had to pick up insulation and we needed to patch a few areas where we found holes. | General Maintenance

## 2022 PM Roof Work Order
WOID | Description | Status | Craft | Location | Area Desc | Area Number | Request Date | Actual Completion Date | Action Taken | Purpose
227424 | Monthly - ROOF INSPECTION-BWES-SEMI ANNUAL - Refer to PM schedule details. | Closed Work Orders | Roof | Bryant Woods ES |  |  | 2022-03-10 01:02 | 2022-05-04 07:32 | These repairs were made per the ATI inspection received on 4/20/22 AH-1 Level 1 (1) PVC roof is designed to hold water. Water disperses within 48 hours. (2) Dark spots on the roof are not mold. This is caused from dirt and normal weathering of the roof. (3) Removed debris and vegetation from the roof. Tightened loose drain bolts Sprayed drain bolts with WD-40 Level 2 Tightened loose drain bolts Sprayed drain bolts with WD-40 Level 3 Removed all debris from the gutter Level 4 (1) PVC roof is designed to hold water. Water disperses within 48 hours. (2) Dark spots on the roof are not mold. This is caused from dirt and normal weathering of the roof. (3) Removed debris and vegetation from the roof. Tightened loose drain bolts Sprayed drain bolts with WD-40 Level 5 (3) Removed debris and vegetation from the roof Tightened loose drain bolts Sprayed drain bolts with WD-40 Level 6 Removed debris and vegetation from the roof Tightened loose drain bolts Sprayed drain bolts with WD-40 Removed debris and vegetation from portable gutters | Preventive Maintenance
253785 | Monthly - ROOF INSPECTION-BWES-SEMI ANNUAL - Refer to PM schedule details. | Closed Work Orders | Roof | Bryant Woods ES |  |  | 2022-09-10 01:17 | 2022-12-01 07:17 | 10/3 Checked building for leaks. Made sure roof drains were clear of debris These repairs were made per the ATI inspection performed on 10/6/22 Level 1 (1) Water disperses within 48 hours (2) Dark spots are not mold. This is caused from dirt and weathering of the roof (3) Removed debris and vegetation from the roof Found three holes in the roof and patched Level 2 (1) Water disperses within 48 hours Removed debris and vegetation from the roof Level 3 Removed debris from the gutter Level 4 (1) Water disperses within 48 hours (2) Dark spots are not mold. This is caused from dirt and weathering of the roof (3) Removed debris and vegetation from the roof Level 5 (1) Water disperses within 48 hours Level 6 Removed debris and vegetation from the roof Removed debris and vegetation from the portable gutters | Preventive Maintenance

## 2022 NON PM Roof Work Order
WOID | Description | Status | Craft | Location | Area Desc | Area Number | Request Date | Actual Completion Date | Action Taken | Purpose
230946 | Roof leak in gym | Closed Work Orders | Roof | Bryant Woods ES |  |  | 2022-04-06 | 2022-04-14 | This is an ongoing leak. We checked the area and it was not dripping. The water comes form the HVAC above the Gym. We called and spoke with Josh to have him check this. | General Maintenance
253128 | Roof leak in the hallway (gym side) between boy's bathroom and water fountain right side of the light near media center | Closed Work Orders | Roof | Bryant Woods ES |  |  | 2022-09-06 | 2022-09-07 14:02 | 9/6 Investigated the leak by the boys bathroom and found multiple holes in the roof in this area but also found multiple holes above the kitchen area. Temporarily patched with caulk. 9/7 Returned and put down permanent patches. Changed out the ceiling tiles and let the custodian know what i had done. | General Maintenance
257343 | hatch stuck | Closed Work Orders | Roof | Bryant Woods ES | Art Room | closet | 2022-10-07 | 2022-10-07 | Beena from ATI sent me a text that the roof hatch was open and would not close. We went to the school and lubed the shocks on the hatch to get it close. The shocks get dry and this happens. | General Maintenance

## 2021 PM Roof Work Order
WOID | Description | Status | Craft | Location | Area Desc | Area Number | Request Date | Actual Completion Date | Action Taken | Purpose
183611 | Monthly - ROOF INSPECTION-BWES-SEMI ANNUAL - Refer to PM schedule details. | Closed Work Orders | Roof | Bryant Woods ES |  |  | 2021-03-10 01:09 | 2021-05-17 07:26 | These repairs were made per the ATI inspection received on 4-20-2021 AH-1 Level 1 (1) PVC roof is designed to hold water, water disperses within 48 hours. Dark spots on the roof are not mold. They are caused from dirt and normal weathering of the roof. (2) removed debris and vegetation from the roof. (3) the dark areas on the wall flashing is caused from dirt and weathering. This is not mold. (4) scratches on the parapet cap are merely cosmetic and not causing leaks. (5) All condensation pipes have been reconnected. (6) abandoned mechanical equipment has been removed from the roof. Level 2 (1) PVC roof is designed to hold water, water disperses within 48 hours. Dark areas on the roof are caused from dirt and normal weathering. This is not mold. Level 3 (7) removed debris from gutter Level 4 (1) PVC roof is designed to hold water, water disperses within 48 hours. Dark spots on the roof are not mold. They are caused from dirt and normal weathering of the roof. (2) removed debris and vegetation from the roof. (3) the dark areas on the wall flashing is caused from dirt and weathering. This is not mold Level 5 (1) PVC roof is designed to hold water. Water disperses within 48 hours. (8) repair patches appear to be in good condition. Level 6 (9) canopy roof appears to be in good condition. Also removed all debris and vegetation from the canopy roof | Preventive Maintenance
205900 | Monthly - ROOF INSPECTION-BWES-SEMI ANNUAL - Refer to PM schedule details. | Closed Work Orders | Roof | Bryant Woods ES |  |  | 2021-09-10 01:03 | 2021-11-12 | These repairs were made per the ATI inspection received on 10/4/21 AH-1 Level 1 (1) PVC roof is designed to hold water. Water disperses within 48 hours. The dark spots on the roof are not mold. This is caused from dirt and normal weathering of the roof. (2) Removed all debris and vegetation from the roof and from around the drains. (3) Removed any debris from the trees close to the roof. We will get these limbs trimmed back. (4) Repaired seam separation by putting a patch over this area. Also found deteriorated caulk at the seams of the coping cap. We cut out the old caulk and replaced it with new. Level 2 (1) PVC roof is designed to hold water. Water disperses within 48 hours. The dark spots on the roof are not mold. This is caused from dirt and normal weathering of the roof. Made sure drains were clear of debris Level 3 Cleaned debris out of the gutter and scupper Level 4 (1) PVC roof is designed to hold water. Water disperses within 48 hours. The dark spots on the roof are not mold. This is caused from dirt and normal weathering of the roof. (2) Removed debris and vegetation from the roof as best we could and made sure the drains were clear of debris. Level 5 (1) PVC roof is designed to hold water. Water disperses within 48 hours. The dark spots on the roof are not mold. This is caused from dirt and normal weathering of the roof. Made sure drains were clear of debris Level 6 (1) PVC roof is designed to hold water. Water disperses within 48 hours. The dark spots on the roof are not mold. This is caused from dirt and normal weathering of the roof. Made sure the drain was clear of debris Emptied out all debris from the gutters on the portables and made sure all the downspouts had splash blocks | Preventive Maintenance

## 2021 NON PM Roof Work Order
WOID | Description | Status | Craft | Location | Area Desc | Area Number | Request Date | Actual Completion Date | Action Taken | Purpose
195177 | small stain area on ceiling tile may be from roof leak can someone please check it out | Closed Work Orders | Roof | Bryant Woods ES | Office | Principal's Office | 2021-06-15 | 2021-06-23 | This leak looks like it's from an exhaust vent. On the roof side, I found that the fan did not fasten to the curb. I also want to clean the adapter bracket corners and reseal them. 6/22 We installed screws to hold down the exhaust fan. We also cleaned and sealed seams with one flash sealant. We changed the ceiling tile. | General Maintenance
198369 | Ceiling is leaking | Closed Work Orders | Roof | Bryant Woods ES | Office | 149 | 2021-07-14 | 2021-09-12 | We checked the area and we found 3 holes in the roof. We patched these and we have to call a seam on the curb into manufacture. Keith changed the ceiling tile. 9/10 Tecta came out and repaired this area while I was on vacation. We came back out to check and the tile was wet. Keith and I rechecked the roof and we found a hole by the walk pad and a few other areas. We patched all the areas and asked the custodian to change the tile on Monday. | General Maintenance
209873 | straighten up the roof on details that need to be repaired. | Closed Work Orders | Roof | Bryant Woods ES | Roof | roof | 2021-10-14 | 2021-11-12 | Started to clean areas and check for problems on the roof areas. We made a ticket to have all the supports for the condensation line replaced. (209821) Dropped off the splash blocks to be installed under the downspouts on the portables. 11/9 Met up with Alex we performed the ATI inspection and adjusted the splash blocks. We had to install a patch over an open seam. | General Maintenance

## 2020 PM Roof Work Order
WOID | Description | Status | Craft | Location | Area Desc | Area Number | Request Date | Actual Completion Date | Action Taken | Purpose
158629 | ATI Inspection | Closed Work Orders | Roof | Bryant Woods ES | Roof |  | 2020-06-19 | 2020-06-19 07:44 | Completed ATI inspection by removing all leafs and debris from rooftop, clearing all drains, and removing any balls from roof. | Preventive Maintenance
166993 | Monthly - ROOF INSPECTION-BWES-SEMI ANNUAL - Refer to PM schedule details. | Closed Work Orders | Roof | Bryant Woods ES |  |  | 2020-09-10 00:53 | 2021-02-08 07:39 | These repairs were made per the ATI inspection received on 10-14-2020 1/21 AH-1 Level 1 (1) the roof is designed to hold water. The dark areas are caused by normal weathering. (2) removed all leaves and debris that fell from trees close to roof. (3) notified HVAC department about EF missing its lid. This is on order and will be installed when it come in. (4) water will pond on parapet cap but disperses within 48 hours not causing any damage. (5) removed folding tent left of the roof. (6) removed fasteners left on the roof. Inspected the area for punctures and did not find any. Level 2 (1) the roof is designed to hold water. The dark areas are caused from normal weathering of the roof. Level 3 (7) removed the debris trapped in the gutter. Level 4 (1) the roof is designed to hold water. The dark areas are caused from normal weathering of the roof. (2) removed all leaves and debris from rooftop that fell from trees close to roof. (8) Ripples in the parapet wall membrane are not causing the roof to leak Or age prematurely. Level 5 (1) the roof is designed to hold water. The dark areas are caused from normal weathering of the roof. Level 6 (9) the canopy roof appears to have some age to is but is otherwise in good condition and not leaking. | Preventive Maintenance
171920 | Leafs and debris on roof | Closed Work Orders | Roof | Bryant Woods ES | Roof |  | 2020-10-29 | 2020-11-04 14:07 | Removed all leafs and debris from rooftop and from around drains | Preventive Maintenance

## 2020 Non PM Roof Work Order
WOID | Description | Status | Craft | Assigned To | Location | Area Desc | Area Number | Request Date | Actual Completion Date | Action Taken | Purpose
163198 | Rain water coming in down through the exhaust fan in the kitchen | Closed Work Orders | Roof | Butler, Robert | Bryant Woods ES |  |  | 2020-08-04 | 2020-08-04 | This leak is from the exhaust fan not having a cap. Sent text to HVAC Dept. they sent out Josh to install a tarp. | General Maintenance
164102 | leak in hall by Cafe | Closed Work Orders | Roof | Butler, Robert | Bryant Woods ES | Hallway/Corridor | by Cafe entrance | 2020-08-12 | 2020-08-27 | We installed patches where we found holes in field sheet. | General Maintenance