## Sheet
Work Order # | Source Site | Source Location | Work Category | WO Status | Created On | Completed | Work requested | Action Taken | Work Type | Origin
0000107806 | Bryant Woods ES |  | Pressure Washing | Declined | 06/11/2026 04:00:47 PM |  | Power washing around the entire building. | We do not clean chalk off the building. | General Custodial | Non-PM
0000107805 | Bryant Woods ES |  | Grounds | New Request | 06/11/2026 03:58:51 PM |  | Garden removal. Over grown weeds that need to be permanently removed. |  |  | Non-PM
0000107801 | Bryant Woods ES | Portable 234 | Doors, Windows and Locks | Archived | 06/11/2026 03:21:54 PM | 06/15/2026 08:11:00 AM | The door lock is hard to open. It's hard to twist the key in the lock. | 6/12 JW Clean and lubricate lock cylinder | Doors and Hardware | Non-PM
0000107127 | Bryant Woods ES |  | Plumbing | Archived | 06/05/2026 09:57:03 AM | 06/15/2026 06:58:00 AM | The sink is coming lose from the wall. | Sr-2 6/12/26 saw sink loose, tightened up screws on career, took off old silicone and installed new silicone, sink is tight to wall and not loose. | Fixtures | Non-PM
0000107121 | Bryant Woods ES |  | Electrical | Archived | 06/05/2026 09:16:19 AM | 06/05/2026 01:33:00 PM | The switch that turns the lights on is cracked. | SG-1 6/5/2026 Replaced cracked single pole switch with new switch | Lighting System | Non-PM
0000107120 | Bryant Woods ES |  | Fire and Safety | Archived | 06/05/2026 09:14:04 AM | 06/05/2026 02:30:00 PM | The screw thar holds the magnet to door fell out | 6/5/26 AK1 reinstalled magnet . | Fire Alarm System | Non-PM
0000106905 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Archived | 06/03/2026 02:29:48 PM | 06/08/2026 10:28:00 AM | Air unit is not working the whole school is running between 79- 84 degrees. | 6/8/26 MK/MR Checked/walked school temps are between 71-74/did notice Cafe unit is heating/cooling/heating/cooling call Dennis S he said he's going to look into way it keeping cycle on/off but over all building temps are good ticket is completed | Air Handling Units (AHU/RTU) | Non-PM
0000106851 | Bryant Woods ES |  | Plumbing | Archived | 06/03/2026 10:09:09 AM | 06/04/2026 08:34:00 AM | Sink was turned off before long weekend, please assess leak on angle valve | 6/3/26-jg-tightened up loose packing nut underneath sink at supply valve | Fixtures | Non-PM
0000106765 | Bryant Woods ES |  | Grounds | Archived | 06/02/2026 01:50:30 PM | 06/02/2026 01:51:00 PM | mow down invasive thistle found at site on previous site inspection | mow canadian thistle down found along teachers parking lot | I.P.M. | Non-PM
0000105575 | Bryant Woods ES |  | Contract Services | In Progress | 05/29/2026 11:32:32 AM |  | Bryant Woods Elem. / Boiler Plant renovation | Thursday 5/28/2026 (SK-1) - Back in February 2026, we met with Larsen to discuss the Boiler heating plant issues found @ Bryant Woods Elem. We determined the best solution is to replace the Weil Mclain cast iron boiler with a Reillo 1500 condensing boiler. Today, we attended a pre-design meeting at Mendenhall. In attendance: Larsen Angel, Rob Lowe & Matt Judge (Building Dynamics) Galen Monti, Ray Miller, & Sam Knight. We discussed the Scope of Work and schedule. Following the meeting, we visited Bryant Woods Elem. to further discuss the project. We met briefly with the Dr. Khaleel Desaque (Principal) to discuss the Boiler project. I did mention the Boiler project can only proceed if the funding allows. Returned to Mendenhall and updated Larsen. 6/15/2026 RM2. Visited site to verify aspects of operation concerning the exhaust fan and hanging unit heater and whether or not the combustion dampers operation is part of there sequence of operation. Veriy location of the hanging heater thermostat. Map location and measurments of equipment within the meachanical room. | Boilers | Non-PM
0000105545 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Archived | 05/29/2026 08:02:05 AM | 05/29/2026 08:03:00 AM | BOILER REPLACEMENT MEETING. | 5/28/2026 RM2. Attended meeting at shop and onsite as instructed . | Boilers | Non-PM
0000105467 | Bryant Woods ES |  | Doors, Windows and Locks | Archived | 05/28/2026 09:46:15 AM | 05/29/2026 02:13:00 PM | Door is not opening properly from the inside. It keeps getting stuck when you try to open it. | 5/29/26 AH-1 DS-3 Rebuilt lock and reinstalled lock. Tested the lock to make sure it was functioning correctly and showed the teacher before leaving the job. | Doors and Hardware | Non-PM
0000105462 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Assigned | 05/28/2026 09:43:28 AM |  | Intake grate on floor was kicked in by student. It needs to be pulled back out. |  | Air Handling Units (AHU/RTU) | Non-PM
0000105438 | Bryant Woods ES |  | Electrical | Archived | 05/28/2026 07:05:50 AM | 05/28/2026 08:49:00 AM | The right side of building has no power | WS-1 5/28/26 Power was restored upon arrival, checked Ok. | Power Systems | Non-PM
0000105212 | Bryant Woods ES |  | Electrical | Archived | 05/22/2026 01:48:18 PM | 05/26/2026 07:21:00 AM | please fifth grade boys and girls bathroom classroom #123 in the media center power is out ,the switch have a safety pin in they thank you. | PB1 5-26-26 Work order request to check power in Room 123 due to report of a paperclip or pin in a switch. Upon arrival, inspected outlets and switches in the room and found no foreign objects present. Traced issue to a tripped lighting breaker in the electrical room. Reset breaker and verified proper operation. All lights and power are working properly at this time. | Power Systems | Non-PM
0000104673 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Archived | 05/19/2026 08:20:13 AM | 05/28/2026 07:40:00 AM | The AC is not worling | CG-1 5-28- Portable unit was low on refrigerant charged system to proper pressures and temperture.Cycled unit through the stat and cycled properly. | Portables | Non-PM
0000104654 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Archived | 05/19/2026 07:36:21 AM | 05/28/2026 08:17:00 AM | The cafeteria is very hot | 5/28/26 MK/CB Checked 58 supply temp/69 degrees in the cafe/with 70 degree setpoint unit is currently working properly | Air Handling Units (AHU/RTU) | Non-PM
0000104653 | Bryant Woods ES |  | Carpentry | Assigned | 05/19/2026 07:34:57 AM |  | The bathroom needs a new paper towel dispenser. |  | Fixtures | Non-PM
0000104459 | Bryant Woods ES |  | Custodial Equipment Repair | Archived | 05/18/2026 07:33:55 AM | 05/18/2026 11:38:00 AM | Wheel on auto scrubber is broke and needs replacing. | Replaced drive wheels on 17/20 scrubber | General Custodial | Non-PM
0000104016 | Bryant Woods ES |  | Doors, Windows and Locks | Archived | 05/13/2026 07:25:24 AM | 05/14/2026 01:04:00 PM | Need 2 set of master keys to work entire building interior and exterior | Kk2 5/14/26 Cut and stamped keys Gave keys to Al he put in box for Robin Hodges to pick up | Doors and Hardware | Non-PM
0000103580 | Bryant Woods ES |  | Custodial Equipment Repair | Archived | 05/07/2026 07:54:40 AM | 05/11/2026 07:06:00 AM | The burnisher is not charging and the ground is broke on the plug. | Replaced ground prong on Speed Gleam charger cord. Machine is charging fine, floater didn't know where the power button was located. | General Custodial | Non-PM
0000103543 | Bryant Woods ES |  | Grounds | Archived | 05/06/2026 07:48:57 PM | 05/21/2026 02:12:00 PM | underneath picnic tables need trimming | Weed eated front circle and under picnic tables. |  | Non-PM
0000103388 | Bryant Woods ES |  | Plumbing | Archived | 05/05/2026 01:15:57 PM | 05/20/2026 06:47:00 AM | The water fountain is leaking when you try to drink from it. | Sr-2 5/19/26 saw nothing leaking on fountain | Drinking Fountains | Non-PM
0000103356 | Bryant Woods ES |  | Doors, Windows and Locks | Archived | 05/05/2026 10:17:18 AM | 05/05/2026 02:21:00 PM | The lock is not working properly. The staff is getting locked in the bathroom. | DG1 5/5/26 repaired lock | Doors and Hardware | Non-PM
0000103339 | Bryant Woods ES |  | Plumbing | Archived | 05/05/2026 08:31:37 AM | 05/20/2026 06:47:00 AM | The two way connector cut switch is broke. | Sr-2 5/19/26 installed new two way hose connection on faucet on the outside mop sink | Fixtures | Non-PM
0000102894 | Bryant Woods ES |  | Custodial Equipment Repair | Archived | 05/01/2026 06:09:04 AM | 05/01/2026 06:10:00 AM | Check all summer equipment to make sure everything is in good working condition. | All summer equipment in good working condition | General Custodial | Non-PM
0000101938 | Bryant Woods ES |  | Electrical | Archived | 04/27/2026 10:19:05 PM | 04/28/2026 11:29:00 AM | kindergarten girls bathroom light switch broken off. switch located in custodial office if needed | Replaced broken switch in bathroom. Lights working normally. | Lighting System | Non-PM
0000101883 | Bryant Woods ES |  | Fire and Safety | Archived | 04/27/2026 09:47:03 AM | 04/27/2026 12:24:00 PM | Fire alarm trouble | 4/27/26 TC1 check panel found in monitoring trouble for CO/Smoke maintenance alert, locate smoke need Siga PCOS, check obsolete smoke, order replacement part, pick up from distributor, call out system, undo old install new, reboot system facp is normal, also provide A126 CAT 45 keys to custodian | Fire Alarm System | Non-PM
0000101665 | Bryant Woods ES |  | Carpentry | Archived | 04/24/2026 10:39:00 AM | 05/08/2026 11:35:00 AM | The paper towel dispenser needs to be fixed. | 5/6 mp2 went to school and replaced dispenser as requested | Fixtures | Non-PM
0000101592 | Bryant Woods ES |  | Grounds | Archived | 04/23/2026 10:27:36 PM | 04/23/2026 10:30:00 PM | Repair sidewalk along student drop off area. | Repaired sidewalk along student drop off area. JB | Concrete Work-Grounds | Non-PM
0000101552 | Bryant Woods ES |  | Carpentry | Archived | 04/23/2026 11:46:47 AM | 05/01/2026 03:35:00 PM | Two holes at the bottom of the gym closet need to be patched up. | 5/1 ed1 and mp2 went to school and looked at job. Patched toes as requested | Interior Surfaces | Non-PM
0000101531 | Bryant Woods ES |  | Pest Control | Archived | 04/23/2026 09:41:39 AM | 04/24/2026 01:32:00 PM | Two mouse holes in the gym closet need to be filled as soon as possible. | Inspected gym storage closet. Sealed hole in wall. Need carpentry to repair wall and floor |  | Non-PM
0000101454 | Bryant Woods ES |  | Plumbing | In Progress | 04/22/2026 12:19:36 PM |  | Faucet needs to be fixed. Water still runs after it's turned off. | 5/4/26-BT1- a new faucet needs to be ordered. I put a hose splitter on for the time being in order to conserve water and prevent an emergency call out. 5/19/26-BT1- Replaced one cartridge on the hot side. Cold iso valve did not hold. The one handle is also stripped. | Fixtures | Non-PM
0000101452 | Bryant Woods ES |  | Pest Control | Archived | 04/22/2026 12:15:26 PM | 04/24/2026 01:34:00 PM | Alot of ants in the classroom. | Inspected classroom for ant activity. Keep food in sealed containers and refrain from eating in classrooms. Use alcohol wipes to clean counters. |  | Non-PM
0000101451 | Bryant Woods ES |  | Pest Control | Duplicate | 04/22/2026 12:14:05 PM |  | Urgent: Mice feces was all over the gym floor when I swept it this morning. |  |  | Non-PM
0000101373 | Bryant Woods ES |  | Fire and Safety | Archived | 04/21/2026 10:29:08 PM | 04/23/2026 02:03:00 PM | door missing magnet to keep door open... magnet part is missing 3/4 grade hallway | 4/23/26 AK1 repaired/replaced broken mag piece with a good used one. | Fire Alarm System | Non-PM
0000101101 | Bryant Woods ES |  | Heating/Ventilation /Air Conditioning | Archived | 04/20/2026 07:53:44 AM | 05/15/2026 06:42:00 AM | LOW BUILDING HEATING WATER TEMPERATURE ALARM STATUS. | 4/20/2026 RM2. Visited site. Checked the equipment for water leaks. Checked the current operating pressure. Checked the building pump operation. Checked the circulator boiler pump operation. Found that the burner controller has no power. Determined that the fuse in the burner disconnect was blown. Replaced the fuse. Checked the combustion damper operation. Checked the burner controller sequence of operation. Checked the gas valve operation. Checked the current operating pressure. Monitored operation. Trended boiler status. 4/21/2026 RM2. Return to site. Replaced blown fuse. Checked burner motor capacitor, which is reading below specifications. Will search for suitable replacement capacitor or combustion motor. Searched and found a used but good capacitor in the salvaged parts at ARL. Returned to BWES and swapped the capacitors. Monitored operation. Went back to ARL to compare motor model numbers with the salvaged motor stock to check for compatible replacements. 4/22/2026 RM2. Signed myself out at the HVAC office. Fueled service van M-33 @ the Rec and Parks fuel pump on Oakland Mills Rd. Visited site checked the county heating equipment current operating statuses remotely via BAS. Checked the equipment onsite current operating status. Monitored operation. Traced wireing from disconnect to terminal block to motor fuse holder and l1 on the boiler control subase. Tightened subase connections. Motor fuse does not blow which may indicate that other electric circuits or electrical loads are the reason for the intermittent fuses blowing. Referenced Fireye Flame Monitor operator manual. Was directed to respond to issue at CCES by SK. Will return and continue when time permits. 4/23/2026 RM2. Signed myself out at the HVAC office. Visited site. Checked the county heating equipment current operating statuses remotely via BAS. Checked equipment onsite for water leaks. Checked the building pump operation. Checked the boiler circulator pump operation. Checked the combustion damper operation. Checked the boiler sequence of operation. Checked the gas valve operation. Flushed the low water cut off float chamber. Monitored operation. Filled in Asset Essentials ticket. | Boilers | Non-PM
0000100835 | Bryant Woods ES |  | Plumbing | Duplicate | 04/17/2026 02:04:24 PM |  | rm 112 sink clogged. very slow drain | RM3 - 4/22/26 - Duplicate to 97257 |  | Non-PM
0000100712 | Bryant Woods ES |  | Custodial Equipment Repair | Archived | 04/16/2026 09:36:06 PM | 04/17/2026 01:50:00 PM | red light stays on. changed bag check hoses and lines. no clogs | Unclogged lower hose | General Custodial | Non-PM
0000100515 | Bryant Woods ES |  | Fire and Safety | Archived | 04/15/2026 01:25:53 PM | 04/15/2026 11:06:00 AM |  |  | Security Cameras | Non-PM
0000099897 | Bryant Woods ES |  | Grounds | Archived | 04/09/2026 09:08:22 AM | 04/13/2026 01:49:00 PM | while outside notice dig holes around play area. Also the sidewalk on side of the building needs repair.... Pics Attch. | Filled in holes with topsoil | Sidewalks | Non-PM
0000099302 | Bryant Woods ES |  | Grounds | Archived | 04/01/2026 08:32:52 PM | 04/01/2026 08:34:00 PM | Paint parking lots and bus loops. | Painted parking lots and bus loop. | Parking Lots | Non-PM
0000099299 | Bryant Woods ES |  | Custodial Equipment Repair | Archived | 04/01/2026 05:21:09 PM | 04/06/2026 09:22:00 AM | wet vac does not turn on after plugged in | Rewired power switch. adjusted strain relief. | General Custodial | Non-PM
0000099298 | Bryant Woods ES |  | Custodial Equipment Repair | Archived | 04/01/2026 05:19:38 PM | 04/06/2026 09:24:00 AM | left wheel is off.... wheel is located in custodail office | Installed new e clip on wheel to hold it in place. | General Custodial | Non-PM
0000099294 | Bryant Woods ES |  | Grounds | Archived | 04/01/2026 02:26:21 PM | 04/01/2026 02:26:00 PM | Remove fall tree next to pathway in back of school | Removed downed tree and took it to the landfill | Tree | Non-PM